## Global_Tags
Symbol | Type | Address | Description
PS1 | BOOL | 400.00 | PROCESS STARTED
ALARMCANCEL | BOOL | 0.00 | ALARM CANCEL
SCADA_ALRM_CNCL | BOOL | 233.00 | SCADA Remote Alarm Cancel
I101 | BOOL | 1.01 | PUMP P72 FAULT RELAY
I001 | BOOL | 0.01 | PROCES START/STOP
CS1 | BOOL | 420.00 | CIP STARTED
PS2 | BOOL | 400.02 | START P116, P76
PS3 | BOOL | 400.04 | START BALANCE TANK EXTRACT PUMP (P64)
I102 | BOOL | 1.02 | PUMP P64 FAULT RELAY
PS4 | BOOL | 400.06 | START VACUUM
SCADA_STRT_PRO | BOOL | 233.01 | SCADA Remote Process Start Stop
PS4TIMER_Status | BOOL | TIM203 | DELAY AFTER VACUUM
PS5 | BOOL | 400.08 | BEGIN VACUUM MONITORING
PS6 | BOOL | 400.10 | START BALANCE TANK PUMP
VACUUM | CHANNEL | DM510 | Separator Vacuum
GREATER_THAN | BOOL | 255.05 | System Greater Than (GE) Flag
EQUALS | BOOL | 255.06 | System Equals (EQ) Flag
PS7 | BOOL | 400.12 | SYSTEM IN RECIRCULATION
SEP_LEVEL | CHANNEL | DM520 | Separator Level
LESS_THAN | BOOL | 255.07 | System Less Than (LE) Flag
PS7TIMER_Status | BOOL | TIM205 | DELAY BEFORE STEAM
PS8 | BOOL | 400.14 | POSITION VALVES AND START STEAM
I103 | BOOL | 1.03 | PUMP 76 FAULT RELAY
Before_loop | CHANNEL | DM500 | Before Loop Temp
PS9TIMER_Status | BOOL | TIM207 | STERILIZATION TIME
| BOOL | TIM208 | Sterilization Time (more time)
I104_P116_fault | BOOL | 1.04 | PUMP 116 FAULT RELAY
I105_P118_fault | BOOL | 1.05 | PUMP 118 FAULT RELAY
WASHOUT_Open | BOOL | 1.07 | WASHOUT PLATE OPEN "2.04 from Chem PLC"
SEP_HI_LEVEL | BOOL | 470.08 | SEPERATOR HIGH LEVEL
START_P116 | BOOL | 1.08 | START P-116 FROM CHEMETATOR PANEL
BTLOW | BOOL | 500.00 | B.T > 10%
PS12TIMER_Status | BOOL | TIM209 | DELAY FOR SEPARATOR LEVEL
WASHOUT_CANDL | BOOL | 1.09 | WASHOUT PLATE CLOSED AND LOCKED
PARK_POSITION | BOOL | 1.10 | CHEMETATOR IN PARK POSITION
SEP_LVL_26PERCENT | BOOL | 470.03
PARK_POSITION | BOOL | 1.10 | CHEMETATOR IN PARK POSITION
SCADA_STRT_CIP | BOOL | 233.03 | SCADA Remote CIP Start / Stop
PS14TIMER_Status | BOOL | TIM211 | DELAY BEFORE MONITORING "keep V-104 open to Drain 2min"
LOWTEMPREC_Status | BOOL | TIM215 | LOW TERMPERATURE MINIMUM REC. TIME
CR200 | BOOL | 2.00 | PRODUCT FEED PUMP STARTER P64
| BOOL | 1.12 | Toggle Switch MAN Position
P116_SCADA_CMD | BOOL | 233.05 | START STOP P116 FROM SCADA P.B
PULSEMINUS1MINUS1 | BOOL | 301.00 | PULSATION 1 SEC. ON 1 SEC. OFF
CIPMINUSPULSEMINUSINDEX_Status | BOOL | CNT050 | INDEX FOR CIP PULSATION
CIPMINUSPULSEMINUSINDEX_PV | CHANNEL | CNT50 | INDEX FOR CIP PULSATION
CIPMINUSPULSATION | CHANNEL | DM99 | CIP PULSATION REFERENCE
CONDUCTIVITY | CHANNEL | DM410 | Conductivity Scaled 0 - 99.99 ms/cm (0 - 9999)
RINSE_STOP_TRIGGER | BOOL | 490.00 | Conductivity less than rinse stop setpoint
CS4 | BOOL | 420.06 | START VOTATOR PULSATION
_10SECONDSMINUS3 | BOOL | 301.03 | 10 SECONDS PULSATION
P68AM | BOOL | 311.00
| BOOL | 490.13 | P116 CIP Inhibit
| BOOL | TIM304 | Rinse #2 Max Time
CS5 | BOOL | 420.08 | START STEAM
P69AM | BOOL | 311.01
| BOOL | TIM298 | Caustic Pump Stop Delay Timer
| BOOL | 490.06 | Caustic Pump Stop Delay
P76AM | BOOL | 311.02
SCADA_PURGE | BOOL | 233.07 | SCADA Remote Plant Purge
| BOOL | 489.15 | Caustic Flow Target Reached
| BOOL | TIM296 | Caustic Max. Duration Timer
CAUSTIC_PUMP_STOP_TRIGGER | BOOL | 490.01 | Caustic Pump Stop Trigger
Add_More_Caustic | BOOL | 490.02 | Add more Caustic
| BOOL | TIM290 | 3 min Timer
CR201 | BOOL | 2.01 | SEPARATOR EXTRACT PUMP P72
CR202 | BOOL | 2.02 | CIP PUMP A STARTER P66
Add_More_Sanitizer | BOOL | 490.03 | Add more Acid
| BOOL | TIM293 | 2 min timer
| BOOL | TIM294 | 3 sec timer
| CHANNEL | 481 | SCADA INPUTS
| CHANNEL | 482 | SCADA OUTPUTS
P116AM | BOOL | 311.03
CR203 | BOOL | 2.03 | CIP PUMP B STARTER P67
CR204 | BOOL | 2.04 | CONDENSATE PUMP STARTER P68
CR205 | BOOL | 2.05 | VACUUM PUMP STARTER P69
CR206 | BOOL | 2.06 | SYSTEM FEED PUMP P76
P118AM | BOOL | 311.04
P117AM | BOOL | 311.05
P119AM | BOOL | 311.06
I002 | BOOL | 0.02 | LAMP TEST
| BOOL | 490.04 | STEP ADVANCE
| BOOL | 490.09 | PreRinse Advance
P64AM | BOOL | 311.09
P72AM | BOOL | 311.10
| BOOL | CNT301 | 1H45m Counter
| BOOL | 494.01 | CIP TOO LONG BIT TO SCADA
STERILMINUSTKMINUSWATE2 | BOOL | 306.00 | STERILE TANK WATER CONTROL
SCADA_CIP_INDC | BOOL | 233.09 | SCADA CIP Running Indicator
CS2 | BOOL | 420.02 | EMPTY BALANCE TANK
| BOOL | CNT007 | Vert. Condenser CIP Counter
CS2TIMER_Status | BOOL | TIM222 | DELAY AFTER LOW LEVEL B.T.
CS3 | BOOL | 420.04 | START LEVEL CONTROL B.T.
CS3TIMER_Status | BOOL | TIM224 | DELAY BEFORE VOTATOR START
CS4TIMER_Status | BOOL | TIM226 | DELAY BEFORE STEAM
CS5TIMER_Status | BOOL | TIM228 | PRERINSE TIME
CS6 | BOOL | 420.10 | PRERINSE COMPLETED
CS7 | BOOL | 420.12 | RINSE RECIRCULATION
CS8 | BOOL | 420.14 | EMPTYING B.T.
CS7TIMER_Status | BOOL | TIM230 | RINSE TIME
| BOOL | 311.11 | V111AM
BT_LVL | BOOL | 500.11 | B.T > 6%
| BOOL | 311.12 | V111 SCADAMAN
CS10TIMER_Status | BOOL | TIM232 | STOP PULSATION VOTATOR
| BOOL | 311.13 | V112AM
CS13TIMER_Status | BOOL | TIM234 | DETERGENT TIME #1
CS13MINUS2TIMER_PV | CHANNEL | TIM235 | DETERGENT TIME
CS13MINUS2TIMER_Status | BOOL | TIM235 | DETERGENT TIME #2
| BOOL | TIM292 | 10 min Timer
ON | BOOL | 253.13 | System Normally On Flag
| BOOL | 424.02 | Sterile TK > 5%
CS14TIMER_Status | BOOL | TIM236 | RINSE RECIRCULATION
| BOOL | 311.14 | V112SCADAMAN
CS15TIMER_Status | BOOL | TIM238 | DELAY BEFORE EMPTYING B.T.
CR207 | BOOL | 2.07 | VOTATOR MOYNO PUMP EAST STARTER P116
CR208 | BOOL | 2.08 | VOTATOR MOYNO PUMP WEST STARTER P118
CS17TIMER_Status | BOOL | TIM240 | SYSTEM IN RECIRCULATION
CR209 | BOOL | 2.09 | VOTATOR CIP PUMP EAST STARTER P117
CS20TIMER_Status | BOOL | TIM242 | ACID TIME 10 MIN.
ON | BOOL | 253.13 | System Normally On Flag
| BOOL | TIM243 | ACID MONTHLY TIME 15 MIN.
CR210 | BOOL | 2.10 | VOTATOR CIP PUMP WEST STARTER P119
CS22TIMER_Status | BOOL | TIM244 | FLUSH TO DRAIN
Acid_Pump | BOOL | 2.13 | Monthly Acid pump
CS23TIMER_Status | BOOL | TIM246 | DELAY BEFORE EMPTYING B.T.
Sanitizer_Pump | BOOL | 2.14 | Daily Sanitizer Pump
ON | BOOL | 253.13 | System Normally On Flag
| BOOL | 424.04 | B.T. < 6%
PS9 | BOOL | 401.00 | START STERILIZATION TIME
| BOOL | TIM311 | P67 OFF Time
OFF | BOOL | 253.14 | System Normally Off Flag
FIRST_SCAN | BOOL | 253.15 | System First Scan Flag
CR300 | BOOL | 3.00 | STOP COMMAND TO CHEM "AT PURGE CYCLE" & STERILIZER IN CIP
SS1 | BOOL | 450.00 | SHUTDOWN STARTED
I003 | BOOL | 0.03 | CIP START/STOP
CR301 | BOOL | 3.01 | VACUUM PUMP 2ND SETPOINT
SS2 | BOOL | 450.02 | STOP FEED
SS3 | BOOL | 450.04 | WATER FEED
CR302 | BOOL | 3.02 | SPARE
SS2TIMER_Status | BOOL | TIM250 | WATER FEED
SS4 | BOOL | 450.06 | EMPTY SEPERATOR
SS3TIMER_Status | BOOL | TIM252 | EMPTY SEPARATOR
SS5 | BOOL | 450.08 | REBUILT SEP. LEVEL
| CHANNEL | DM521 | Separator Level Setpoint
| BOOL | 470.04 | Separator < 10%
SS6 | BOOL | 450.10 | WATER TO DRAIN
SS5TIMER_Status | BOOL | TIM254 | DELAY BEFORE WATER TO DRAIN
SS7 | BOOL | 450.12 | SYSTEM IN RECIRCULATION
SS6TIMER_Status | BOOL | TIM256 | SYSTEM IN RECIRCULATION
BTGRTRTHAN55PERCENT | BOOL | 500.04 | B.T. > 55% "STOP P76"
SS8 | BOOL | 450.14 | EMPTY STERILE TANK
SS7TIMER_Status | BOOL | TIM258 | EMPTY STERILE TANK
PS10 | BOOL | 401.02 | SYSTEM STERILE (READY FOR PRODUCTION)
SS9TIMER_Status | BOOL | TIM260 | RECIRCULATION
PS11 | BOOL | 401.04 | TRANSITION TO PRODUCT
SS10TIMER_Status | BOOL | TIM262 | STOP STEAM
PS12 | BOOL | 401.06 | START FEED CONTROL
SS11TIMER_Status | BOOL | TIM264 | SHUTDOWN COMPLETED
BTGRTRTHAN25PERCENT | BOOL | 500.02 | B.T. > 25% "START P76"
WS3 | BOOL | 455.08 | WATER STEP #3
WS1 | BOOL | 455.02 | WATER STEP #1
WS1TIMER_Status | BOOL | TIM270 | COMPENSATE WATER
WS2 | BOOL | 455.04 | WATER STEP #2
WS2TIMER_Status | BOOL | TIM272 | CLOSE WATER VALVE
PS13 | BOOL | 401.08 | WAITING FOR SEPARATOR LOW LEVEL
SLCS3 | BOOL | 465.08 | RESET
SLCS1 | BOOL | 465.02
SLCS1TIMER_Status | BOOL | TIM274 | DELAY BEFORE RECIR.
SLCS2 | BOOL | 465.04 | SYSTEM IN RECIRCULATION V4.15 ENERG.
SLCS2TIMER_Status | BOOL | TIM275 | RECIRCULATION TIME
BTLEVEL | CHANNEL | 111 | BALANCE TANK LEVEL
BT_LL_5PERCENT | BOOL | 500.10 | BALANCE TANK LOW 5%
BT_35PERCENT | BOOL | 504.05 | BALANC TANK LEVEL >35%
Caustic_Pump | BOOL | 2.15 | Caustic Pump
TO_control_PU64 | BOOL | 232.02 | TO OPERATE PRODUCT FEED PUMP STARTER P64
CR303 | BOOL | 3.03 | SEPARATOR EXTRACT PUMP 2ND SETPOINT
BTK_level_75PERCENT | BOOL | 500.12 | BALANCE TANK LEVEL > 75%
| BOOL | 504.07 | BALANCE TANK LEVEL > 68%
CIPMINUSOVERFLOW | BOOL | 500.05 | BALANCE TANK CIP OVERFLOW
BTLESSTHAN15PERCENT | BOOL | 500.13 | B.T. < 15%
W_Votator_Temp | CHANNEL | 104 | West votator Temp
STLEVEL | CHANNEL | 112 | STERILE TANK LEVEL
| BOOL | 424.03 | Sterile TK < 30%
PS14 | BOOL | 401.10 | SYSTEM IN FORWARD
PS15 | BOOL | 401.12 | BEGIN PRODUCTION MONITORING
PS18 | BOOL | 401.14 | MINIMUM RECIRCULATION TIME FOR LOW TEMP ALARM
CS9 | BOOL | 421.00 | FLUSH TO DRAIN
CS10 | BOOL | 421.02 | SYSTEM IN RECIRCULATION
BTHIGHALARM | BOOL | 500.08 | BALANCE TANK HIGH LEVEL ALARM
BTHIGHCANCEL | BOOL | 500.09 | BALANCE TANK HIGH LEVEL ALARM CANCEL
I004 | BOOL | 0.04 | STERILE TANK WATER VALVE ON/OFF
CR304 | BOOL | 3.04 | HOT WATER 2ND SETPOINT
BTLOWALARM | BOOL | 500.06 | BALANCE TANK LOW LEVEL ALARM 5%
BT_LOW1 | BOOL | 500.01 | BALANCE TANK LEVEL <20% ALARM
BT_LOW2 | BOOL | 500.03 | BALANCE TANK LEVEL <15%
BTLOWACK | BOOL | 500.07 | BALANCE TANK LOW LEVEL ALARM CANCEL
CS11 | BOOL | 421.04 | RECIRCULATION COMPLETED
CS12 | BOOL | 421.06 | DETERGENT WASH
CS12 | BOOL | 421.06 | DETERGENT WASH
CS13 | BOOL | 421.08 | EMPTY B.T.
CS13 | BOOL | 421.08 | EMPTY B.T.
CS14 | BOOL | 421.10 | RINSE #2
STLOWALARMLATCH | BOOL | 504.00 | STERILE TANK LOW LEVEL ALARM LATCH
STLOWLEVELRES | BOOL | 504.01 | STERILE TANK LOW LEVEL ALARM RESET <8%
CS14 | BOOL | 421.10 | RINSE #2
I005 | BOOL | 0.05 | PUMP 116 (P.B)
TO_control_P72 | BOOL | 232.03 | TO OPERATE SEPARATOR PUMP STARTER P72
MEMORYMINUSERROR | BOOL | 272.12 | MEMORY ERROR
After_Loop | CHANNEL | 101 | After Loop Temp
AfterLoopLESSTHAN140 | BOOL | 470.12 | After loop temp <140c
BeforeLoopLESSTHAN140 | BOOL | 470.14 | Before loop temp <140c
SS6ATIMER_Status | BOOL | TIM257 | 10 min delay before stop steam,and P64,72
V88SCADAMAN | BOOL | 312.00
V77SCADAMAN | BOOL | 312.01
V90SCADAMAN | BOOL | 312.02
V101ABSCADAMAN | BOOL | 312.03
V93SCADAMAN | BOOL | 312.04
CS15 | BOOL | 421.12 | RINSE RECIRCULATION
CS15 | BOOL | 421.12 | RINSE RECIRCULATION
CS16 | BOOL | 421.14 | EMPTYING B.T.
SS9 | BOOL | 451.00 | IN FORWARD
SS10 | BOOL | 451.02 | RECIRCULATION
| BOOL | 3.06 | Vert. Condenser Cooling Water (V116) 1=off
CR307 | BOOL | 3.07 | to P117 controller to change speed durring caustic rinse (step-3)
TIMER1_Status | BOOL | TIM001 | PULSE 1 SEC. ON 1 SEC. OFF
TIMER0_Status | BOOL | TIM000 | PULSE 1 SEC. ON 1 SEC. OFF
SS11 | BOOL | 451.04 | STOP STEAM
_1MINUSSECONDSMINUS2_Status | BOOL | TIM003 | 10 SECONDS PULSATION
_10SECONDS_Status | BOOL | TIM002 | 10 SECONDS PULSATION
I006 | BOOL | 0.06 | VOTATOR FEED PUMP WEST 118
CR308 | BOOL | 3.08 | AUDIBLE ALARM BUZZER
P207CNT | BOOL | 305.00 | COUNTER PUMP 207
CNTP207_Status | BOOL | CNT010 | COUNTER P207
CNTP207_PV | CHANNEL | CNT10 | COUNTER P207
ONDIVIDEOFFP207 | BOOL | 305.01 | ON/OFF PUMP P207
I007 | BOOL | 0.07 | PLANT PURGE
P208CNT | BOOL | 305.03 | PUMP P208 WEST RESET
CNTP208_Status | BOOL | CNT011 | COUNTER P208
CNTP208_PV | CHANNEL | CNT11 | COUNTER P208
ONDIVIDEOFFP208 | BOOL | 305.04 | ON/OFF PUMP P208
VTLAMP | BOOL | 305.10 | VOTATOR LAMP FLASH
_5sec_delay_Status | BOOL | TIM266 | Sterile tank low level 3 sec delay timer
I008 | BOOL | 0.08 | EMERGENCY STOP
STERILMINUSTKMINUSWATER_Status | BOOL | CNT012 | STERILE TANK WATER CTRL
STERILMINUSTKMINUSWATER_PV | CHANNEL | CNT12 | STERILE TANK WATER CTRL
| BOOL | 506.00 | Process Running
| BOOL | 490.14 | P116 1st CIP
P200MINUSPULSE | BOOL | 415.00
V100SCADAMAN | BOOL | 312.05
SS12 | BOOL | 451.06 | SHUTDOWN COMPLETED
V91ABSCADAMAN | BOOL | 312.06
P66AM | BOOL | 310.14
V103SCADAMAN | BOOL | 312.07
V104SCADAMAN | BOOL | 312.08
P67AM | BOOL | 310.15
V106SCADAMAN | BOOL | 312.09
V108ABSCADAMAN | BOOL | 312.11
P66_CIP_FlowLow | BOOL | 471.00 | P66 low flow rate durring CIP "Check P66"
| BOOL | TIM308 | Delay for Vert. Condenser Back Flush
CR309 | BOOL | 3.09 | VISUAL ALARM WARNING BEACON
V109ABSCADAMAN | BOOL | 312.12
| BOOL | 471.01 | Seperator Level < 12%
| BOOL | 3.10 | Sterilizer to Ext. Valve
V110SCADAMAN | BOOL | 312.13
P66SCADAMAN | BOOL | 312.14
CIP_MANUAL_PB | BOOL | 491.00 | Manual CIP Selection PB
| BOOL | 3.11 | Vert. Condenser Condensate Return (V114) 1=off
CIP_AUTO_PB | BOOL | 491.01 | Auto CIP Selection PB
P207MINUSPULSE | BOOL | 415.02
CIP_AUTO_MONTHLY_PB | BOOL | 491.02 | Auto Monthly CIP Selection PB
CR312 | BOOL | 3.12 | Vert. Condenser CIP Water (V115)
P67SCADAMAN | BOOL | 312.15
P208MINUSPULSE | BOOL | 415.03
CIP_AUTO_SHORT_PB | BOOL | 491.03 | Auto Short CIP Selection PB
CR313 | BOOL | 3.13 | BCD #2 I/O COMM. OMRON PLC
CS17 | BOOL | 422.00 | FLUSH TO DRAIN
LLST | BOOL | 501.00 | LOW LEVEL STERILE TANK >10%
CR314 | BOOL | 3.14 | BCD #3 I/O COMM. OMRON PLC
CS18 | BOOL | 422.02 | SYSTEM IN RECIRCULATION
| BOOL | 501.01 | Steril TK > 25%
CR315 | BOOL | 3.15 | BCD #4 I/O COMM. OMRON PLC
CS19 | BOOL | 422.04 | OPERATOR START
| BOOL | TIM282 | ACID MONTHLY INJECTION TIMER
CS20 | BOOL | 422.06 | ACID WASH
ACID_INJECTION_DONE | BOOL | TIM280 | Sanitizer injection duration timer
CS20 | BOOL | 422.06 | ACID WASH
CS21 | BOOL | 422.08 | EMPTYING B.T.
P68SCADAMAN | BOOL | 313.00
P69SCADAMAN | BOOL | 313.01
SV400 | BOOL | 4.00 | STERILE TANK WATER VALVE V77
SV401 | BOOL | 4.01 | BALANCE TANK WATER VALVE V88
P76SCADAMAN | BOOL | 313.02
P116SCADAMAN | BOOL | 313.03
P118SCADAMAN | BOOL | 313.04
| CHANNEL | DM501 | Before loop S.P
P117SCADAMAN | BOOL | 313.05
P119SCADAMAN | BOOL | 313.06
BELLMINUSPULSE2_Status | BOOL | CNT005 | 2 PULSES
BELLMINUSPULSE4_Status | BOOL | CNT006 | 4 PULSES
P64SCADAMAN | BOOL | 313.09
P72SCADAMAN | BOOL | 313.10
CS25 | BOOL | 423.00 | STOP FEED
| BOOL | TIM309 | End of Back Flush
CS25 | BOOL | 423.00 | STOP FEED
BCDHASH2 | BOOL | 509.02 | COMMUNICATION TO 2ND OMRON PLC
CS26 | BOOL | 423.02 | ALARM
BCDHASH3 | BOOL | 509.01 | COMMUNICATION TO 2ND OMRON PLC
| BOOL | 423.11 | >3hrs from CIP to Start - DO SHORT CIP
BCDHASH4 | BOOL | 509.00 | COMMUNICATION TO 2ND OMRON PLC
| BOOL | 493.00 | STEP REPEAT PULSE
V77AM | BOOL | 310.01
CS21 | BOOL | 422.08 | EMPTYING B.T.
SPARE_Status | BOOL | TIM265
V88AM | BOOL | 310.00
CS22 | BOOL | 422.10 | RINSE #3
_15Sec_pulse_Status | BOOL | TIM018 | 15 sec pulse every 5 min
V90AM | BOOL | 310.02
CS22 | BOOL | 422.10 | RINSE #3
SV402 | BOOL | 4.02 | BALANCE TANK SPRAY BALL V-90
V101ABAM | BOOL | 310.03
CS23 | BOOL | 422.12 | RINSE RECIRCULATION
SV403 | BOOL | 4.03 | CIP PUMP A ISOLATION VALVE V101
LoopTempGRTRTHAN95c | BOOL | 480.03 | loop temp >/= 95c stop steam
LoopTempLESSTHAN85c | BOOL | 480.04 | loop temp </= 85c start steam
SV404 | BOOL | 4.04 | STEAM VALVE V93
V93AM | BOOL | 310.04
CS23 | BOOL | 422.12 | RINSE RECIRCULATION
SV405_BPV | BOOL | 4.05 | Back Pressure Valve Air supply V-98
SV406 | BOOL | 4.06 | SEPARATOR VACUUM VALVE V99
V100AM | BOOL | 310.05
CS24 | BOOL | 422.14 | EMPTYING B.T.
SV407 | BOOL | 4.07 | SEPARATOR CIP SPRAY BALL VALVE V100
V91ABAM | BOOL | 310.06
CS24 | BOOL | 422.14 | EMPTYING B.T.
SV408 | BOOL | 4.08 | CIP PUMP B ISOLATION VALVES V91
V103AM | BOOL | 310.07
CIP_MANUAL_SELECTED | BOOL | 492.00 | Manual CIP Selected
SV409 | BOOL | 4.09 | RECIRC VALVE V103
LA511 | BOOL | 5.11 | WATER RINSE #1 LAMP
V104AM | BOOL | 310.08
CIP_AUTO_SELECTED | BOOL | 492.01 | Auto CIP Selected
SV410_V104 | BOOL | 4.10 | V-104 To DRAIN VALVE V-90
V411MINUSPULSE | BOOL | 415.08
V411PULSE | BOOL | HR0.01 | TO KEEP THE STERILE TANK SPRAY VALVE OPEN FOR 60Sec
V106AM | BOOL | 310.09
CIP_AUTO_MONTHLY_SELECTED | BOOL | 492.02 | Auto Monthly CIP Selected
SV411 | BOOL | 4.11 | STERILE TANK CIP SPRAY BALL V-106
SV412 | BOOL | 4.12 | STERILE TANK BLOCKING VALVE V107 (N/O)
V108ABAM | BOOL | 310.11
CIP_AUTO_SHORT_SELECTED | BOOL | 492.03 | Auto Short CIP Selected
SV413 | BOOL | 4.13 | CIP PUMP EAST VOTATOR ISOLATION VALVE V108
V109ABAM | BOOL | 310.12
HIGHPRESSW | BOOL | 502.00 | HIGH PRESSURE SWITCH ALARM
SV414 | BOOL | 4.14 | CIP PUMP WEST VOTATOR ISOLATION VALVE V109
SV415_V110 | BOOL | 4.15 | BALANCE TANK CIP RETURN VALVE 110 N.O to drian N.C to BTK
V110AM | BOOL | 310.13
PRESWAK | BOOL | 502.01 | PRESURE ALARM ACK
| BOOL | 506.01 | Shut Down in Progress
MLST | BOOL | 501.02 | MID LEVEL STERILE TANK >15%
STK_25PERCENT | BOOL | 501.03 | Steril Tank >30%
| BOOL | 506.02 | CIP in Progress
HLST | BOOL | 501.04 | HIGH LEVEL STERILE TANK >80%
STK_35PERCENT | BOOL | 501.05 | Steril Tank >35%
| BOOL | 0.09 | CIP CAUSTIC PULSE
LA500 | BOOL | 5.00 | ALARM ACKNOWLEDGE LAMP
LA501 | BOOL | 5.01 | PROCESS BUTTON LAMP
LA502 | BOOL | 5.02 | CIP BUTTON LAMP
LA503 | BOOL | 5.03 | PRODUCTION PURGE LAMP
LA504 | BOOL | 5.04 | STERILE TANK HOT WATER VALVE LAMP
LA505 | BOOL | 5.05 | VOTATOR FEED PUMP EAST LAMP
LA506 | BOOL | 5.06 | VOTATOR FEED PUMP WEST LAMP
SEP_LVL_65PERCENT | BOOL | 470.13 | Seperator Level <65%
Stop_P67 | BOOL | 480.02 | Sep Level < 11%
LA507 | BOOL | 5.07 | VACUUM/LIQUID LEVEL LAMP
LA508 | BOOL | 5.08 | WATER STERILIZATION TRANSITION LAMP
LA509 | BOOL | 5.09 | STERILIZATION RANSITION LAMP
LA510 | BOOL | 5.10 | GELATIN STERILIZATION LAMP
LA512 | BOOL | 5.12 | CAUSTIC/DETERGENT LAMP
LA513 | BOOL | 5.13 | WATER RINSE #2 LAMP
LA514 | BOOL | 5.14 | BALANCE TANK LEVEL ALARM LAMP
LA515 | BOOL | 5.15 | SEPARATOR LEVEL ALARM LAMP
| BOOL | 506.03 | Chemetator Parked
| BOOL | 506.05 | Unknown State / Crashed
| BOOL | 506.06 | CIP TOO LONG
| BOOL | 506.07 | SFTK Oulet Valve Open
LA600 | BOOL | 6.00 | STERILE TANK LEVEL ALARM
LA601 | BOOL | 6.01 | VARIABLE SPED DRIVE FAULT LAMP
STLOWALARM | BOOL | 501.06 | STERILE TANK LOW LEVEL ALARM <6%
| BOOL | 504.10 | Toggle Switch MAN Indication
| BOOL | 504.11 | Chemetator Reclaim Tank Pump O/L
| BOOL | 504.12 | Chemetator Reclaim Tank HI Level
LA602 | BOOL | 6.02 | ACID WASH LAMP
LA603 | BOOL | 6.03 | WATER RINSE #3 LAMP
LA604 | BOOL | 6.04 | LOW TEMPERATURE ALARM LAMP
LA605 | BOOL | 6.05 | HIGH PRESSURE ALARM LAMP
| BOOL | 6.06 | CIP RETURN TO STERILE TANK V111
| BOOL | 6.07 | CIP REtURN TO DRAIN V112
| BOOL | 6.08 | Vert. Condenser Drain Valve (V113)
BIT609 | BOOL | 6.09 | 2 LINE DISPLAY BIT#0
ALWAYSMINUSFALSE | BOOL | 300.00
AC1C1UL | CHANNEL | DM1001 | UPPER LIMIT
AC1C1LL | CHANNEL | DM1000 | LOWER LIMIT
AC1C1 | BOOL | 100.02 | SCALING ON
AC1C2UL | CHANNEL | DM1003 | UPPERLIMIT
AC1C2LL | CHANNEL | DM1002 | LOWER LIMIT
AC1C2 | BOOL | 100.03 | SCALING ON
AC1C3UL | CHANNEL | DM1005 | UPPER LIMIT
AC1C3LL | CHANNEL | DM1004 | LOWER LIMIT
AC1C3 | BOOL | 100.04 | SCALING ON
AC1C4UL | CHANNEL | DM1007 | UPPER LIMIT
AC1C4LL | CHANNEL | DM1006 | LOWER LIMIT
AC1C4 | BOOL | 100.05 | SCALING ON
AC2C1UL | CHANNEL | DM1101 | UPPER LIMIT
AC2C1LL | CHANNEL | DM1100 | LOWER LIMIT
AC2C1 | BOOL | 110.02 | SCALING ON
AC2C2UL | CHANNEL | DM1103 | UPPER LIMIT
AC2C2LL | CHANNEL | DM1102 | LOWER LIMIT
AC2C2 | BOOL | 110.03 | SCALING ON
AC2C3UL | CHANNEL | DM1105 | UPPER LIMIT
AC2C3LL | CHANNEL | DM1104 | LOWER LIMIT
AC2C3 | BOOL | 110.04 | SCALING ON
AC2C4UL | CHANNEL | DM1107 | UPPER LIMIT
AC2C4LL | CHANNEL | DM1106 | LOWER LIMIT
AC2C4 | BOOL | 110.05 | SCALING ON
_2MINUSLINESMINUSDISPLAY | CHANNEL | 510 | 2 LINES DISPLAY
LOWTEMPALARM | BOOL | 502.04 | LOW TEMP. ALARM
_2NDMINUSOMRONMINUSPLC | CHANNEL | 508 | COMMUNICATION WITH 2ND OMRON PLC
STLOWACK | BOOL | 501.07 | STERILE TANK LOW LEVEL ALARM CANCEL
| BOOL | 493.01 | STEP REPEAT
LOWTEMPACK | BOOL | 502.05 | LOW TEMPERATURE ALARM ACKNOWLEDGE
STHIGHALARM | BOOL | 501.08 | STERILE TANK HIGH ALARM >90%
VSDALARM | BOOL | 503.00 | VSD ALARM
SEPLEVELALARM | BOOL | 502.08 | SEPARATOR LEVEL ALARM
BIT610 | BOOL | 6.10 | 2 LINE DISPLAY BIT#1
| CHANNEL | DM420 | Sterilizer Status
BIT611 | BOOL | 6.11 | 2 LINE DISPLAY BIT#2
BIT612 | BOOL | 6.12 | 2 LINE DISPLAY BIT#3
BIT613 | BOOL | 6.13 | 2 LINE DISPLAY BIT#4
BIT614 | BOOL | 6.14 | 2 LINE DISPLAY BIT#5
| BOOL | CNT305 | CIP Duration Counter
BIT615 | BOOL | 6.15 | 2 LINE DISPLAY BIT#6
VSDALARMACK | BOOL | 503.01 | VSD ALARM ACKNOWLEDGE
EQUALS | BOOL | 255.06 | System Equals (EQ) Flag
| CHANNEL | DM501 | Before loop S.P
| CHANNEL | DM521 | Separator Level Setpoint
LESS_THAN | BOOL | 255.07 | System Less Than (LE) Flag
| BOOL | 503.02 | Balance Tank level >13% durring water Sterilization (open V-88 10%~13%)
Before_loop | CHANNEL | DM500 | Before Loop Temp
VACUUM | CHANNEL | DM510 | Separator Vacuum
SEP_LEVEL | CHANNEL | DM520 | Separator Level
GEL_FLOWRATE | CHANNEL | DM530 | Gelly flow rate L/m
GREATER_THAN | BOOL | 255.05 | System Greater Than (GE) Flag
CS1 | BOOL | 420.00 | CIP STARTED
Before_loop | CHANNEL | DM500 | Before Loop Temp
GREATER_THAN | BOOL | 255.05 | System Greater Than (GE) Flag
EQUALS | BOOL | 255.06 | System Equals (EQ) Flag
LoopTempGRTRTHAN95c | BOOL | 480.03 | loop temp >/= 95c stop steam
LESS_THAN | BOOL | 255.07 | System Less Than (LE) Flag
LoopTempLESSTHAN85c | BOOL | 480.04 | loop temp </= 85c start steam
PS1 | BOOL | 400.00 | PROCESS STARTED
STHIGHCANCEL | BOOL | 501.09 | STERILE TANK HIGH LEVEL ALARM CANCEL
SS1 | BOOL | 450.00 | SHUTDOWN STARTED
Batch_Start | BOOL | 500.15 | Batch Start Gelly on belt "CIP timming Report"
| BOOL | 503.10 | BT > 30%
STEAM_PRESS_TX | CHANNEL | 113 | steam pressure input 0-150 psi
CIP_CAUSTIC_FLOW | CHANNEL | 114 | CIP Caustic Flowmeter (0 - 25 lpm)
COND_TX1 | CHANNEL | 103 | Conductivity meter 0-100 ms/cm
| BOOL | 315.04 | Steam Press. Alarm
CONDUCTIVITY | CHANNEL | DM410 | Conductivity Scaled 0 - 99.99 ms/cm (0 - 9999)
CIP_STEPS | CHANNEL | DM910 | CIP SQUENCE TO DRIER PLC TO SET P117 P66 SPEED
CS7 | BOOL | 420.12 | RINSE RECIRCULATION
STER_LVL_8PERCENT | BOOL | 501.10 | STER TK < 8% "Open V77 to clean out Chemetator"
VERYMINUSLOWMINUSLEVEL | BOOL | 501.11 | RESET VOTATOR LOW LEVEL STERILE TANK 3%
SEPALARMACK | BOOL | 502.09 | SEPARATOR LEVEL ALARM ACK.
VACUUMALARM | BOOL | 502.12 | LOW VACUUM ALARM
CS5 | BOOL | 420.08 | START STEAM
CS8 | BOOL | 420.14 | EMPTYING B.T.
STTKLESS90PERCENT | BOOL | 501.12 | STERILE TANK LEVEL LESS THAN 90%
STTKHIGH85PERCENT | BOOL | 501.13 | STERILE TANK LEVEL greater than 85%
VACUUMALARACK | BOOL | 502.13 | VACUUM ALARM ACK.
| BOOL | 502.14 | Balance Tank > 35%
| BOOL | 502.15 | Balance Tank > 45%
_15Sec_pulse_Status | BOOL | TIM018 | 15 sec pulse every 5 min
_10_Sec_pulse_Status | BOOL | TIM017 | 10 sec pulse every 10 min
CS4 | BOOL | 420.06 | START VOTATOR PULSATION
| BOOL | 503.11 | BT < 6%
GEL_FLOWRATE | CHANNEL | DM530 | Gelly flow rate L/m
STKLEVELGRTRTHAN95PERCENT | BOOL | 501.14 | STERILE TANK LEVEL MORE THAN 95%
BTLEVEL | CHANNEL | 111 | BALANCE TANK LEVEL
BTLESSTHAN15PERCENT | BOOL | 500.13 | B.T. < 15%
BTGRTRTHAN30PERCENT | BOOL | 500.14
I012 | BOOL | 0.12 | SEPARATOR PRESSURE S.P. SWITCH
| BOOL | 489.15 | Caustic Flow Target Reached

## IO_Cards
Omron Card | I/O Address | Shorthand | Capacity | Purpose
ID212 | 0000 | 0 | 16 pts | Digital Input
ID212 | 0001 | 1 | 16 pts | Digital Input
OC225 | 0002 | 2 | 16 pts | Digital Output
OC225 | 0003 | 3 | 16 pts | Digital Output
OC225 | 0004 | 4 | 16 pts | Digital Output
OC225 | 0005 | 5 | 16 pts | Digital Output
OC225 | 0006 | 6 | 16 pts | Digital Output
AD001 | 0100 | 100 | 4 pts | Analog Input
AD001 | 0110 | 110 | 4 pts | Analog Input

## Tag_Translation
Symbol | Type | Address | Description | AB_Address | AB_Type | AB_IO_Address
PS1 | BOOL | 400.00 | PROCESS STARTED
I001 | BOOL | 0.01 | PROCES START/STOP
SCADA_STRT_PRO | BOOL | 233.01 | SCADA Remote Process Start Stop
SS12 | BOOL | 451.06 | SHUTDOWN COMPLETED
I008 | BOOL | 0.08 | EMERGENCY STOP
CS1 | BOOL | 420.00 | CIP STARTED
PS2 | BOOL | 400.02 | START P116, P76
PS3 | BOOL | 400.04 | START BALANCE TANK EXTRACT PUMP (P64)
STER_LVL_8PERCENT | BOOL | 501.10 | STER TK < 8% "Open V77 to clean out Chemetator"
PS4 | BOOL | 400.06 | START VACUUM
| BOOL | 503.10 | BT > 30%
PS4TIMER_Status | BOOL | TIM203 | DELAY AFTER VACUUM
PS5 | BOOL | 400.08 | BEGIN VACUUM MONITORING
PS6 | BOOL | 400.10 | START BALANCE TANK PUMP
VACUUM | CHANNEL | DM510 | Separator Vacuum
GREATER_THAN | BOOL | 255.05 | System Greater Than (GE) Flag
EQUALS | BOOL | 255.06 | System Equals (EQ) Flag
PS7 | BOOL | 400.12 | SYSTEM IN RECIRCULATION
SEP_LEVEL | CHANNEL | DM520 | Separator Level
LESS_THAN | BOOL | 255.07 | System Less Than (LE) Flag
PS7TIMER_Status | BOOL | TIM205 | DELAY BEFORE STEAM
PS8 | BOOL | 400.14 | POSITION VALVES AND START STEAM
PS9 | BOOL | 401.00 | START STERILIZATION TIME
Before_loop | CHANNEL | DM500 | Before Loop Temp
PS9TIMER_Status | BOOL | TIM207 | STERILIZATION TIME
| BOOL | TIM208 | Sterilization Time (more time)
PS10 | BOOL | 401.02 | SYSTEM STERILE (READY FOR PRODUCTION)
PS11 | BOOL | 401.04 | TRANSITION TO PRODUCT
WASHOUT_Open | BOOL | 1.07 | WASHOUT PLATE OPEN "2.04 from Chem PLC"
SEP_HI_LEVEL | BOOL | 470.08 | SEPERATOR HIGH LEVEL
PS12 | BOOL | 401.06 | START FEED CONTROL
BTLOW | BOOL | 500.00 | B.T > 10%
PS12TIMER_Status | BOOL | TIM209 | DELAY FOR SEPARATOR LEVEL
PS13 | BOOL | 401.08 | WAITING FOR SEPARATOR LOW LEVEL
PS15 | BOOL | 401.12 | BEGIN PRODUCTION MONITORING
SEP_LVL_26PERCENT | BOOL | 470.03
PS14 | BOOL | 401.10 | SYSTEM IN FORWARD
SCADA_STRT_CIP | BOOL | 233.03 | SCADA Remote CIP Start / Stop
PS14TIMER_Status | BOOL | TIM211 | DELAY BEFORE MONITORING "keep V-104 open to Drain 2min"
LOWTEMPREC_Status | BOOL | TIM215 | LOW TERMPERATURE MINIMUM REC. TIME
LOWTEMPALARM | BOOL | 502.04 | LOW TEMP. ALARM
PS18 | BOOL | 401.14 | MINIMUM RECIRCULATION TIME FOR LOW TEMP ALARM
ON | BOOL | 253.13 | System Normally On Flag
_10SECONDSMINUS3 | BOOL | 301.03 | 10 SECONDS PULSATION
CIPMINUSPULSEMINUSINDEX_Status | BOOL | CNT050 | INDEX FOR CIP PULSATION
CIPMINUSPULSEMINUSINDEX_PV | CHANNEL | CNT50 | INDEX FOR CIP PULSATION
CIPMINUSPULSATION | CHANNEL | DM99 | CIP PULSATION REFERENCE
CONDUCTIVITY | CHANNEL | DM410 | Conductivity Scaled 0 - 99.99 ms/cm (0 - 9999)
RINSE_STOP_TRIGGER | BOOL | 490.00 | Conductivity less than rinse stop setpoint
CS4 | BOOL | 420.06 | START VOTATOR PULSATION
CS14 | BOOL | 421.10 | RINSE #2
CS16 | BOOL | 421.14 | EMPTYING B.T.
| BOOL | 490.13 | P116 CIP Inhibit
| BOOL | TIM304 | Rinse #2 Max Time
CS5 | BOOL | 420.08 | START STEAM
CS12 | BOOL | 421.06 | DETERGENT WASH
| BOOL | TIM298 | Caustic Pump Stop Delay Timer
| BOOL | 490.06 | Caustic Pump Stop Delay
CS13 | BOOL | 421.08 | EMPTY B.T.
OFF | BOOL | 253.14 | System Normally Off Flag
| BOOL | 489.15 | Caustic Flow Target Reached
| BOOL | TIM296 | Caustic Max. Duration Timer
CAUSTIC_PUMP_STOP_TRIGGER | BOOL | 490.01 | Caustic Pump Stop Trigger
Add_More_Caustic | BOOL | 490.02 | Add more Caustic
| BOOL | TIM290 | 3 min Timer
CS20 | BOOL | 422.06 | ACID WASH
CS21 | BOOL | 422.08 | EMPTYING B.T.
Add_More_Sanitizer | BOOL | 490.03 | Add more Acid
| BOOL | TIM293 | 2 min timer
| BOOL | TIM294 | 3 sec timer
| CHANNEL | 481 | SCADA INPUTS
| CHANNEL | 482 | SCADA OUTPUTS
CIP_MANUAL_PB | BOOL | 491.00 | Manual CIP Selection PB
CIP_MANUAL_SELECTED | BOOL | 492.00 | Manual CIP Selected
CIP_AUTO_SELECTED | BOOL | 492.01 | Auto CIP Selected
CIP_AUTO_MONTHLY_SELECTED | BOOL | 492.02 | Auto Monthly CIP Selected
CIP_AUTO_SHORT_SELECTED | BOOL | 492.03 | Auto Short CIP Selected
CIP_AUTO_PB | BOOL | 491.01 | Auto CIP Selection PB
CIP_AUTO_MONTHLY_PB | BOOL | 491.02 | Auto Monthly CIP Selection PB
CIP_AUTO_SHORT_PB | BOOL | 491.03 | Auto Short CIP Selection PB
I003 | BOOL | 0.03 | CIP START/STOP
| BOOL | 490.04 | STEP ADVANCE
| BOOL | 490.09 | PreRinse Advance
WASHOUT_CANDL | BOOL | 1.09 | WASHOUT PLATE CLOSED AND LOCKED
PARK_POSITION | BOOL | 1.10 | CHEMETATOR IN PARK POSITION
| BOOL | CNT301 | 1H45m Counter
| BOOL | 494.01 | CIP TOO LONG BIT TO SCADA
| BOOL | 506.07 | SFTK Oulet Valve Open
CS26 | BOOL | 423.02 | ALARM
CS2 | BOOL | 420.02 | EMPTY BALANCE TANK
| BOOL | CNT007 | Vert. Condenser CIP Counter
CS2TIMER_Status | BOOL | TIM222 | DELAY AFTER LOW LEVEL B.T.
CS3 | BOOL | 420.04 | START LEVEL CONTROL B.T.
CS3TIMER_Status | BOOL | TIM224 | DELAY BEFORE VOTATOR START
CS4TIMER_Status | BOOL | TIM226 | DELAY BEFORE STEAM
CS5TIMER_Status | BOOL | TIM228 | PRERINSE TIME
CS6 | BOOL | 420.10 | PRERINSE COMPLETED
CS7 | BOOL | 420.12 | RINSE RECIRCULATION
CS8 | BOOL | 420.14 | EMPTYING B.T.
CS7TIMER_Status | BOOL | TIM230 | RINSE TIME
CS9 | BOOL | 421.00 | FLUSH TO DRAIN
BT_LVL | BOOL | 500.11 | B.T > 6%
CS10 | BOOL | 421.02 | SYSTEM IN RECIRCULATION
CS10TIMER_Status | BOOL | TIM232 | STOP PULSATION VOTATOR
CS11 | BOOL | 421.04 | RECIRCULATION COMPLETED
CS13TIMER_Status | BOOL | TIM234 | DETERGENT TIME #1
CS13MINUS2TIMER_PV | CHANNEL | TIM235 | DETERGENT TIME
CS13MINUS2TIMER_Status | BOOL | TIM235 | DETERGENT TIME #2
| BOOL | TIM292 | 10 min Timer
| BOOL | 493.00 | STEP REPEAT PULSE
| BOOL | 424.02 | Sterile TK > 5%
CS14TIMER_Status | BOOL | TIM236 | RINSE RECIRCULATION
CS15 | BOOL | 421.12 | RINSE RECIRCULATION
CS15TIMER_Status | BOOL | TIM238 | DELAY BEFORE EMPTYING B.T.
CS17 | BOOL | 422.00 | FLUSH TO DRAIN
CS18 | BOOL | 422.02 | SYSTEM IN RECIRCULATION
CS17TIMER_Status | BOOL | TIM240 | SYSTEM IN RECIRCULATION
CS19 | BOOL | 422.04 | OPERATOR START
CS20TIMER_Status | BOOL | TIM242 | ACID TIME 10 MIN.
| BOOL | 493.01 | STEP REPEAT
| BOOL | TIM243 | ACID MONTHLY TIME 15 MIN.
CS22 | BOOL | 422.10 | RINSE #3
CS22TIMER_Status | BOOL | TIM244 | FLUSH TO DRAIN
CS23 | BOOL | 422.12 | RINSE RECIRCULATION
CS23TIMER_Status | BOOL | TIM246 | DELAY BEFORE EMPTYING B.T.
CS24 | BOOL | 422.14 | EMPTYING B.T.
CS25 | BOOL | 423.00 | STOP FEED
| BOOL | 424.04 | B.T. < 6%
VERYMINUSLOWMINUSLEVEL | BOOL | 501.11 | RESET VOTATOR LOW LEVEL STERILE TANK 3%
| BOOL | TIM311 | P67 OFF Time
| BOOL | 423.11 | >3hrs from CIP to Start - DO SHORT CIP
SCADA_CIP_INDC | BOOL | 233.09 | SCADA CIP Running Indicator
| BOOL | 3.10 | Sterilizer to Ext. Valve
SS1 | BOOL | 450.00 | SHUTDOWN STARTED
I007 | BOOL | 0.07 | PLANT PURGE
SCADA_PURGE | BOOL | 233.07 | SCADA Remote Plant Purge
SS2 | BOOL | 450.02 | STOP FEED
SS3 | BOOL | 450.04 | WATER FEED
| BOOL | 503.11 | BT < 6%
SS2TIMER_Status | BOOL | TIM250 | WATER FEED
SS4 | BOOL | 450.06 | EMPTY SEPERATOR
SS3TIMER_Status | BOOL | TIM252 | EMPTY SEPARATOR
SS5 | BOOL | 450.08 | REBUILT SEP. LEVEL
| CHANNEL | DM521 | Separator Level Setpoint
| BOOL | 470.04 | Separator < 10%
SS6 | BOOL | 450.10 | WATER TO DRAIN
SS5TIMER_Status | BOOL | TIM254 | DELAY BEFORE WATER TO DRAIN
SS7 | BOOL | 450.12 | SYSTEM IN RECIRCULATION
SS6TIMER_Status | BOOL | TIM256 | SYSTEM IN RECIRCULATION
BTGRTRTHAN55PERCENT | BOOL | 500.04 | B.T. > 55% "STOP P76"
SS8 | BOOL | 450.14 | EMPTY STERILE TANK
SS7TIMER_Status | BOOL | TIM258 | EMPTY STERILE TANK
SS9 | BOOL | 451.00 | IN FORWARD
SS9TIMER_Status | BOOL | TIM260 | RECIRCULATION
SS10 | BOOL | 451.02 | RECIRCULATION
SS10TIMER_Status | BOOL | TIM262 | STOP STEAM
SS11 | BOOL | 451.04 | STOP STEAM
SS11TIMER_Status | BOOL | TIM264 | SHUTDOWN COMPLETED
BTGRTRTHAN25PERCENT | BOOL | 500.02 | B.T. > 25% "START P76"
WS3 | BOOL | 455.08 | WATER STEP #3
WS1 | BOOL | 455.02 | WATER STEP #1
WS1TIMER_Status | BOOL | TIM270 | COMPENSATE WATER
WS2 | BOOL | 455.04 | WATER STEP #2
WS2TIMER_Status | BOOL | TIM272 | CLOSE WATER VALVE
LLST | BOOL | 501.00 | LOW LEVEL STERILE TANK >10%
SLCS3 | BOOL | 465.08 | RESET
SLCS1 | BOOL | 465.02
SLCS1TIMER_Status | BOOL | TIM274 | DELAY BEFORE RECIR.
SLCS2 | BOOL | 465.04 | SYSTEM IN RECIRCULATION V4.15 ENERG.
SLCS2TIMER_Status | BOOL | TIM275 | RECIRCULATION TIME
BTLEVEL | CHANNEL | 111 | BALANCE TANK LEVEL
BT_LL_5PERCENT | BOOL | 500.10 | BALANCE TANK LOW 5%
BT_35PERCENT | BOOL | 504.05 | BALANC TANK LEVEL >35%
| BOOL | 502.14 | Balance Tank > 35%
| BOOL | 502.15 | Balance Tank > 45%
| BOOL | 503.02 | Balance Tank level >13% durring water Sterilization (open V-88 10%~13%)
BTK_level_75PERCENT | BOOL | 500.12 | BALANCE TANK LEVEL > 75%
| BOOL | 504.07 | BALANCE TANK LEVEL > 68%
CIPMINUSOVERFLOW | BOOL | 500.05 | BALANCE TANK CIP OVERFLOW
BTLESSTHAN15PERCENT | BOOL | 500.13 | B.T. < 15%
W_Votator_Temp | CHANNEL | 104 | West votator Temp
STLEVEL | CHANNEL | 112 | STERILE TANK LEVEL
| BOOL | 424.03 | Sterile TK < 30%
MLST | BOOL | 501.02 | MID LEVEL STERILE TANK >15%
HLST | BOOL | 501.04 | HIGH LEVEL STERILE TANK >80%
STK_25PERCENT | BOOL | 501.03 | Steril Tank >30%
| BOOL | 501.01 | Steril TK > 25%
STK_35PERCENT | BOOL | 501.05 | Steril Tank >35%
BTHIGHALARM | BOOL | 500.08 | BALANCE TANK HIGH LEVEL ALARM
BTHIGHCANCEL | BOOL | 500.09 | BALANCE TANK HIGH LEVEL ALARM CANCEL
ALARMCANCEL | BOOL | 0.00 | ALARM CANCEL
SCADA_ALRM_CNCL | BOOL | 233.00 | SCADA Remote Alarm Cancel
BTLOWALARM | BOOL | 500.06 | BALANCE TANK LOW LEVEL ALARM 5%
BT_LOW1 | BOOL | 500.01 | BALANCE TANK LEVEL <20% ALARM
BT_LOW2 | BOOL | 500.03 | BALANCE TANK LEVEL <15%
BTLOWACK | BOOL | 500.07 | BALANCE TANK LOW LEVEL ALARM CANCEL
STHIGHALARM | BOOL | 501.08 | STERILE TANK HIGH ALARM >90%
STTKLESS90PERCENT | BOOL | 501.12 | STERILE TANK LEVEL LESS THAN 90%
STTKHIGH85PERCENT | BOOL | 501.13 | STERILE TANK LEVEL greater than 85%
STKLEVELGRTRTHAN95PERCENT | BOOL | 501.14 | STERILE TANK LEVEL MORE THAN 95%
STHIGHCANCEL | BOOL | 501.09 | STERILE TANK HIGH LEVEL ALARM CANCEL
STLOWALARM | BOOL | 501.06 | STERILE TANK LOW LEVEL ALARM <6%
STLOWALARMLATCH | BOOL | 504.00 | STERILE TANK LOW LEVEL ALARM LATCH
STLOWLEVELRES | BOOL | 504.01 | STERILE TANK LOW LEVEL ALARM RESET <8%
STLOWACK | BOOL | 501.07 | STERILE TANK LOW LEVEL ALARM CANCEL
I012 | BOOL | 0.12 | SEPARATOR PRESSURE S.P. SWITCH
HIGHPRESSW | BOOL | 502.00 | HIGH PRESSURE SWITCH ALARM
PRESWAK | BOOL | 502.01 | PRESURE ALARM ACK
After_Loop | CHANNEL | 101 | After Loop Temp
AfterLoopLESSTHAN140 | BOOL | 470.12 | After loop temp <140c
BeforeLoopLESSTHAN140 | BOOL | 470.14 | Before loop temp <140c
SS6ATIMER_Status | BOOL | TIM257 | 10 min delay before stop steam,and P64,72
LOWTEMPACK | BOOL | 502.05 | LOW TEMPERATURE ALARM ACKNOWLEDGE
SEPLEVELALARM | BOOL | 502.08 | SEPARATOR LEVEL ALARM
SEPALARMACK | BOOL | 502.09 | SEPARATOR LEVEL ALARM ACK.
VACUUMALARM | BOOL | 502.12 | LOW VACUUM ALARM
VACUUMALARACK | BOOL | 502.13 | VACUUM ALARM ACK.
I105_P118_fault | BOOL | 1.05 | PUMP 118 FAULT RELAY
I104_P116_fault | BOOL | 1.04 | PUMP 116 FAULT RELAY
I103 | BOOL | 1.03 | PUMP 76 FAULT RELAY
I102 | BOOL | 1.02 | PUMP P64 FAULT RELAY
I101 | BOOL | 1.01 | PUMP P72 FAULT RELAY
VSDALARM | BOOL | 503.00 | VSD ALARM
VSDALARMACK | BOOL | 503.01 | VSD ALARM ACKNOWLEDGE
TIMER1_Status | BOOL | TIM001 | PULSE 1 SEC. ON 1 SEC. OFF
TIMER0_Status | BOOL | TIM000 | PULSE 1 SEC. ON 1 SEC. OFF
PULSEMINUS1MINUS1 | BOOL | 301.00 | PULSATION 1 SEC. ON 1 SEC. OFF
_1MINUSSECONDSMINUS2_Status | BOOL | TIM003 | 10 SECONDS PULSATION
_10SECONDS_Status | BOOL | TIM002 | 10 SECONDS PULSATION
I005 | BOOL | 0.05 | PUMP 116 (P.B)
P116_SCADA_CMD | BOOL | 233.05 | START STOP P116 FROM SCADA P.B
P207CNT | BOOL | 305.00 | COUNTER PUMP 207
CNTP207_Status | BOOL | CNT010 | COUNTER P207
CNTP207_PV | CHANNEL | CNT10 | COUNTER P207
ONDIVIDEOFFP207 | BOOL | 305.01 | ON/OFF PUMP P207
I006 | BOOL | 0.06 | VOTATOR FEED PUMP WEST 118
P208CNT | BOOL | 305.03 | PUMP P208 WEST RESET
CNTP208_Status | BOOL | CNT011 | COUNTER P208
CNTP208_PV | CHANNEL | CNT11 | COUNTER P208
ONDIVIDEOFFP208 | BOOL | 305.04 | ON/OFF PUMP P208
VTLAMP | BOOL | 305.10 | VOTATOR LAMP FLASH
_5sec_delay_Status | BOOL | TIM266 | Sterile tank low level 3 sec delay timer
I004 | BOOL | 0.04 | STERILE TANK WATER VALVE ON/OFF
STERILMINUSTKMINUSWATER_Status | BOOL | CNT012 | STERILE TANK WATER CTRL
STERILMINUSTKMINUSWATER_PV | CHANNEL | CNT12 | STERILE TANK WATER CTRL
STERILMINUSTKMINUSWATE2 | BOOL | 306.00 | STERILE TANK WATER CONTROL
| BOOL | 490.14 | P116 1st CIP
P200MINUSPULSE | BOOL | 415.00
TO_control_PU64 | BOOL | 232.02 | TO OPERATE PRODUCT FEED PUMP STARTER P64
| BOOL | 471.01 | Seperator Level < 12%
TO_control_P72 | BOOL | 232.03 | TO OPERATE SEPARATOR PUMP STARTER P72
P66AM | BOOL | 310.14
P66SCADAMAN | BOOL | 312.14
CR202 | BOOL | 2.02 | CIP PUMP A STARTER P66
P67AM | BOOL | 310.15
P67SCADAMAN | BOOL | 312.15
CR203 | BOOL | 2.03 | CIP PUMP B STARTER P67
P68AM | BOOL | 311.00
| BOOL | TIM308 | Delay for Vert. Condenser Back Flush
P68SCADAMAN | BOOL | 313.00
CR204 | BOOL | 2.04 | CONDENSATE PUMP STARTER P68
P69AM | BOOL | 311.01
P69SCADAMAN | BOOL | 313.01
CR205 | BOOL | 2.05 | VACUUM PUMP STARTER P69
CR206 | BOOL | 2.06 | SYSTEM FEED PUMP P76
P76AM | BOOL | 311.02
P76SCADAMAN | BOOL | 313.02
START_P116 | BOOL | 1.08 | START P-116 FROM CHEMETATOR PANEL
P207MINUSPULSE | BOOL | 415.02
P116AM | BOOL | 311.03
P116SCADAMAN | BOOL | 313.03
CR207 | BOOL | 2.07 | VOTATOR MOYNO PUMP EAST STARTER P116
P208MINUSPULSE | BOOL | 415.03
P118AM | BOOL | 311.04
P118SCADAMAN | BOOL | 313.04
CR208 | BOOL | 2.08 | VOTATOR MOYNO PUMP WEST STARTER P118
P117AM | BOOL | 311.05
P117SCADAMAN | BOOL | 313.05
CR209 | BOOL | 2.09 | VOTATOR CIP PUMP EAST STARTER P117
P119AM | BOOL | 311.06
P119SCADAMAN | BOOL | 313.06
CR210 | BOOL | 2.10 | VOTATOR CIP PUMP WEST STARTER P119
| BOOL | TIM282 | ACID MONTHLY INJECTION TIMER
Acid_Pump | BOOL | 2.13 | Monthly Acid pump
ACID_INJECTION_DONE | BOOL | TIM280 | Sanitizer injection duration timer
Sanitizer_Pump | BOOL | 2.14 | Daily Sanitizer Pump
Caustic_Pump | BOOL | 2.15 | Caustic Pump
CR300 | BOOL | 3.00 | STOP COMMAND TO CHEM "AT PURGE CYCLE" & STERILIZER IN CIP
CR301 | BOOL | 3.01 | VACUUM PUMP 2ND SETPOINT
SV400 | BOOL | 4.00 | STERILE TANK WATER VALVE V77
SV401 | BOOL | 4.01 | BALANCE TANK WATER VALVE V88
CR302 | BOOL | 3.02 | SPARE
CR303 | BOOL | 3.03 | SEPARATOR EXTRACT PUMP 2ND SETPOINT
CR304 | BOOL | 3.04 | HOT WATER 2ND SETPOINT
| CHANNEL | DM501 | Before loop S.P
| BOOL | 3.06 | Vert. Condenser Cooling Water (V116) 1=off
CR307 | BOOL | 3.07 | to P117 controller to change speed durring caustic rinse (step-3)
BELLMINUSPULSE2_Status | BOOL | CNT005 | 2 PULSES
BELLMINUSPULSE4_Status | BOOL | CNT006 | 4 PULSES
CR308 | BOOL | 3.08 | AUDIBLE ALARM BUZZER
CR309 | BOOL | 3.09 | VISUAL ALARM WARNING BEACON
| BOOL | 3.11 | Vert. Condenser Condensate Return (V114) 1=off
| BOOL | TIM309 | End of Back Flush
CR312 | BOOL | 3.12 | Vert. Condenser CIP Water (V115)
BCDHASH2 | BOOL | 509.02 | COMMUNICATION TO 2ND OMRON PLC
CR313 | BOOL | 3.13 | BCD #2 I/O COMM. OMRON PLC
BCDHASH3 | BOOL | 509.01 | COMMUNICATION TO 2ND OMRON PLC
CR314 | BOOL | 3.14 | BCD #3 I/O COMM. OMRON PLC
BCDHASH4 | BOOL | 509.00 | COMMUNICATION TO 2ND OMRON PLC
CR315 | BOOL | 3.15 | BCD #4 I/O COMM. OMRON PLC
V77AM | BOOL | 310.01
V77SCADAMAN | BOOL | 312.01
SPARE_Status | BOOL | TIM265
V88AM | BOOL | 310.00
V88SCADAMAN | BOOL | 312.00
_15Sec_pulse_Status | BOOL | TIM018 | 15 sec pulse every 5 min
V90AM | BOOL | 310.02
V90SCADAMAN | BOOL | 312.02
SV402 | BOOL | 4.02 | BALANCE TANK SPRAY BALL V-90
V101ABAM | BOOL | 310.03
V101ABSCADAMAN | BOOL | 312.03
SV403 | BOOL | 4.03 | CIP PUMP A ISOLATION VALVE V101
LoopTempGRTRTHAN95c | BOOL | 480.03 | loop temp >/= 95c stop steam
LoopTempLESSTHAN85c | BOOL | 480.04 | loop temp </= 85c start steam
SV404 | BOOL | 4.04 | STEAM VALVE V93
V93AM | BOOL | 310.04
V93SCADAMAN | BOOL | 312.04
SV405_BPV | BOOL | 4.05 | Back Pressure Valve Air supply V-98
SV406 | BOOL | 4.06 | SEPARATOR VACUUM VALVE V99
V100AM | BOOL | 310.05
V100SCADAMAN | BOOL | 312.05
SV407 | BOOL | 4.07 | SEPARATOR CIP SPRAY BALL VALVE V100
V91ABAM | BOOL | 310.06
V91ABSCADAMAN | BOOL | 312.06
SV408 | BOOL | 4.08 | CIP PUMP B ISOLATION VALVES V91
V103AM | BOOL | 310.07
V103SCADAMAN | BOOL | 312.07
SV409 | BOOL | 4.09 | RECIRC VALVE V103
LA511 | BOOL | 5.11 | WATER RINSE #1 LAMP
V104AM | BOOL | 310.08
V104SCADAMAN | BOOL | 312.08
SV410_V104 | BOOL | 4.10 | V-104 To DRAIN VALVE V-90
V411MINUSPULSE | BOOL | 415.08
V411PULSE | BOOL | HR0.01 | TO KEEP THE STERILE TANK SPRAY VALVE OPEN FOR 60Sec
V106AM | BOOL | 310.09
V106SCADAMAN | BOOL | 312.09
SV411 | BOOL | 4.11 | STERILE TANK CIP SPRAY BALL V-106
SV412 | BOOL | 4.12 | STERILE TANK BLOCKING VALVE V107 (N/O)
V108ABAM | BOOL | 310.11
V108ABSCADAMAN | BOOL | 312.11
SV413 | BOOL | 4.13 | CIP PUMP EAST VOTATOR ISOLATION VALVE V108
V109ABAM | BOOL | 310.12
V109ABSCADAMAN | BOOL | 312.12
SV414 | BOOL | 4.14 | CIP PUMP WEST VOTATOR ISOLATION VALVE V109
SV415_V110 | BOOL | 4.15 | BALANCE TANK CIP RETURN VALVE 110 N.O to drian N.C to BTK
V110AM | BOOL | 310.13
V110SCADAMAN | BOOL | 312.13
| BOOL | 6.06 | CIP RETURN TO STERILE TANK V111
| BOOL | 311.11 | V111AM
| BOOL | 311.12 | V111 SCADAMAN
| BOOL | 6.07 | CIP REtURN TO DRAIN V112
| BOOL | 311.13 | V112AM
| BOOL | 311.14 | V112SCADAMAN
I002 | BOOL | 0.02 | LAMP TEST
LA500 | BOOL | 5.00 | ALARM ACKNOWLEDGE LAMP
LA501 | BOOL | 5.01 | PROCESS BUTTON LAMP
LA502 | BOOL | 5.02 | CIP BUTTON LAMP
LA503 | BOOL | 5.03 | PRODUCTION PURGE LAMP
LA504 | BOOL | 5.04 | STERILE TANK HOT WATER VALVE LAMP
LA505 | BOOL | 5.05 | VOTATOR FEED PUMP EAST LAMP
LA506 | BOOL | 5.06 | VOTATOR FEED PUMP WEST LAMP
SEP_LVL_65PERCENT | BOOL | 470.13 | Seperator Level <65%
Stop_P67 | BOOL | 480.02 | Sep Level < 11%
LA507 | BOOL | 5.07 | VACUUM/LIQUID LEVEL LAMP
LA508 | BOOL | 5.08 | WATER STERILIZATION TRANSITION LAMP
LA509 | BOOL | 5.09 | STERILIZATION RANSITION LAMP
LA510 | BOOL | 5.10 | GELATIN STERILIZATION LAMP
LA512 | BOOL | 5.12 | CAUSTIC/DETERGENT LAMP
LA513 | BOOL | 5.13 | WATER RINSE #2 LAMP
LA514 | BOOL | 5.14 | BALANCE TANK LEVEL ALARM LAMP
LA515 | BOOL | 5.15 | SEPARATOR LEVEL ALARM LAMP
LA600 | BOOL | 6.00 | STERILE TANK LEVEL ALARM
LA601 | BOOL | 6.01 | VARIABLE SPED DRIVE FAULT LAMP
LA602 | BOOL | 6.02 | ACID WASH LAMP
LA603 | BOOL | 6.03 | WATER RINSE #3 LAMP
LA604 | BOOL | 6.04 | LOW TEMPERATURE ALARM LAMP
LA605 | BOOL | 6.05 | HIGH PRESSURE ALARM LAMP
| BOOL | 1.12 | Toggle Switch MAN Position
| BOOL | 504.10 | Toggle Switch MAN Indication
| BOOL | 504.11 | Chemetator Reclaim Tank Pump O/L
| BOOL | 504.12 | Chemetator Reclaim Tank HI Level
| BOOL | 6.08 | Vert. Condenser Drain Valve (V113)
BIT609 | BOOL | 6.09 | 2 LINE DISPLAY BIT#0
BIT610 | BOOL | 6.10 | 2 LINE DISPLAY BIT#1
BIT611 | BOOL | 6.11 | 2 LINE DISPLAY BIT#2
BIT612 | BOOL | 6.12 | 2 LINE DISPLAY BIT#3
BIT613 | BOOL | 6.13 | 2 LINE DISPLAY BIT#4
BIT614 | BOOL | 6.14 | 2 LINE DISPLAY BIT#5
BIT615 | BOOL | 6.15 | 2 LINE DISPLAY BIT#6
ALWAYSMINUSFALSE | BOOL | 300.00
AC1C1UL | CHANNEL | DM1001 | UPPER LIMIT
AC1C1LL | CHANNEL | DM1000 | LOWER LIMIT
AC1C1 | BOOL | 100.02 | SCALING ON
AC1C2UL | CHANNEL | DM1003 | UPPERLIMIT
AC1C2LL | CHANNEL | DM1002 | LOWER LIMIT
AC1C2 | BOOL | 100.03 | SCALING ON
AC1C3UL | CHANNEL | DM1005 | UPPER LIMIT
AC1C3LL | CHANNEL | DM1004 | LOWER LIMIT
AC1C3 | BOOL | 100.04 | SCALING ON
AC1C4UL | CHANNEL | DM1007 | UPPER LIMIT
AC1C4LL | CHANNEL | DM1006 | LOWER LIMIT
AC1C4 | BOOL | 100.05 | SCALING ON
AC2C1UL | CHANNEL | DM1101 | UPPER LIMIT
AC2C1LL | CHANNEL | DM1100 | LOWER LIMIT
AC2C1 | BOOL | 110.02 | SCALING ON
AC2C2UL | CHANNEL | DM1103 | UPPER LIMIT
AC2C2LL | CHANNEL | DM1102 | LOWER LIMIT
AC2C2 | BOOL | 110.03 | SCALING ON
AC2C3UL | CHANNEL | DM1105 | UPPER LIMIT
AC2C3LL | CHANNEL | DM1104 | LOWER LIMIT
AC2C3 | BOOL | 110.04 | SCALING ON
AC2C4UL | CHANNEL | DM1107 | UPPER LIMIT
AC2C4LL | CHANNEL | DM1106 | LOWER LIMIT
AC2C4 | BOOL | 110.05 | SCALING ON
_2MINUSLINESMINUSDISPLAY | CHANNEL | 510 | 2 LINES DISPLAY
MEMORYMINUSERROR | BOOL | 272.12 | MEMORY ERROR
_2NDMINUSOMRONMINUSPLC | CHANNEL | 508 | COMMUNICATION WITH 2ND OMRON PLC
P64AM | BOOL | 311.09
P64SCADAMAN | BOOL | 313.09
CR200 | BOOL | 2.00 | PRODUCT FEED PUMP STARTER P64
P72AM | BOOL | 311.10
P72SCADAMAN | BOOL | 313.10
CR201 | BOOL | 2.01 | SEPARATOR EXTRACT PUMP P72
| BOOL | 506.00 | Process Running
| CHANNEL | DM420 | Sterilizer Status
| BOOL | 506.01 | Shut Down in Progress
| BOOL | 506.06 | CIP TOO LONG
| BOOL | 506.02 | CIP in Progress
| BOOL | 506.03 | Chemetator Parked
| BOOL | CNT305 | CIP Duration Counter
| BOOL | 506.05 | Unknown State / Crashed
ON | BOOL | 253.13 | System Normally On Flag
EQUALS | BOOL | 255.06 | System Equals (EQ) Flag
| CHANNEL | DM501 | Before loop S.P
| CHANNEL | DM521 | Separator Level Setpoint
LESS_THAN | BOOL | 255.07 | System Less Than (LE) Flag
FIRST_SCAN | BOOL | 253.15 | System First Scan Flag
Before_loop | CHANNEL | DM500 | Before Loop Temp
VACUUM | CHANNEL | DM510 | Separator Vacuum
SEP_LEVEL | CHANNEL | DM520 | Separator Level
GEL_FLOWRATE | CHANNEL | DM530 | Gelly flow rate L/m
GREATER_THAN | BOOL | 255.05 | System Greater Than (GE) Flag
CS1 | BOOL | 420.00 | CIP STARTED
Before_loop | CHANNEL | DM500 | Before Loop Temp
GREATER_THAN | BOOL | 255.05 | System Greater Than (GE) Flag
EQUALS | BOOL | 255.06 | System Equals (EQ) Flag
LoopTempGRTRTHAN95c | BOOL | 480.03 | loop temp >/= 95c stop steam
LESS_THAN | BOOL | 255.07 | System Less Than (LE) Flag
LoopTempLESSTHAN85c | BOOL | 480.04 | loop temp </= 85c start steam
PS1 | BOOL | 400.00 | PROCESS STARTED
PARK_POSITION | BOOL | 1.10 | CHEMETATOR IN PARK POSITION
SS1 | BOOL | 450.00 | SHUTDOWN STARTED
Batch_Start | BOOL | 500.15 | Batch Start Gelly on belt "CIP timming Report"
ON | BOOL | 253.13 | System Normally On Flag
STEAM_PRESS_TX | CHANNEL | 113 | steam pressure input 0-150 psi
CIP_CAUSTIC_FLOW | CHANNEL | 114 | CIP Caustic Flowmeter (0 - 25 lpm)
COND_TX1 | CHANNEL | 103 | Conductivity meter 0-100 ms/cm
| BOOL | 315.04 | Steam Press. Alarm
CONDUCTIVITY | CHANNEL | DM410 | Conductivity Scaled 0 - 99.99 ms/cm (0 - 9999)
CIP_STEPS | CHANNEL | DM910 | CIP SQUENCE TO DRIER PLC TO SET P117 P66 SPEED
CS7 | BOOL | 420.12 | RINSE RECIRCULATION
CS12 | BOOL | 421.06 | DETERGENT WASH
CS14 | BOOL | 421.10 | RINSE #2
CS20 | BOOL | 422.06 | ACID WASH
CS22 | BOOL | 422.10 | RINSE #3
CS5 | BOOL | 420.08 | START STEAM
CS8 | BOOL | 420.14 | EMPTYING B.T.
CS13 | BOOL | 421.08 | EMPTY B.T.
CS15 | BOOL | 421.12 | RINSE RECIRCULATION
CS21 | BOOL | 422.08 | EMPTYING B.T.
CS23 | BOOL | 422.12 | RINSE RECIRCULATION
CS24 | BOOL | 422.14 | EMPTYING B.T.
_15Sec_pulse_Status | BOOL | TIM018 | 15 sec pulse every 5 min
_10_Sec_pulse_Status | BOOL | TIM017 | 10 sec pulse every 10 min
CS4 | BOOL | 420.06 | START VOTATOR PULSATION
CS25 | BOOL | 423.00 | STOP FEED
GEL_FLOWRATE | CHANNEL | DM530 | Gelly flow rate L/m
P66_CIP_FlowLow | BOOL | 471.00 | P66 low flow rate durring CIP "Check P66"
BTLEVEL | CHANNEL | 111 | BALANCE TANK LEVEL
BTLESSTHAN15PERCENT | BOOL | 500.13 | B.T. < 15%
BTGRTRTHAN30PERCENT | BOOL | 500.14
| BOOL | 0.09 | CIP CAUSTIC PULSE
| BOOL | 489.15 | Caustic Flow Target Reached