## IO_Cards
Omron Card | I/O Address | Shorthand | Capacity | Purpose
AD003 | 0170 |  | 8 ch | Analog Input
TS101 | 0130 |  | 4 ch Temp. | Temperature Sensor
OD219 | 0038 |  | 64 pts | Digital Output
ID217 | 0042 |  | 64 pts | Digital Input
DA004 | 0100 |  | 8 ch | Analog Output
AD003 | 0180 |  | 8 ch | Analog Input
AD003 | 0190 |  | 8 ch | Analog Input
AD001 | 0110 |  | 4 ch | Analog Input
IM212 | 0011 |  | 16 pts | Digital Input

## Global_Symbols
Symbol | Type | Address | Description
| BOOL | 11.04 | feed back from Sterilizer PLC CIP step to change P117 speed durring caustic wash.
| BOOL | 11.05 | Sterilizer Ozone ALM
| BOOL | 11.06 | Sterilizer Ozone Trouble ALM
| BOOL | 39.01 | Hi Speed Contact
| BOOL | 39.08 | Butterfly #1 (N/C) to F/G
| BOOL | 39.09 | Butterfly #2 (N/O) to 7M
| BOOL | 39.11 | Butterfly #4 (N/C) to F/G
| BOOL | 42.01 | Carrier Chiller Comp. #1
| BOOL | 42.02 | Carrier Chiller Comp. #2
| BOOL | 42.03 | Carrier Chiller Comp. #3
| BOOL | 42.04 | Carrier Chiller Comp. #4
| BOOL | 42.05 | Carrier Chiller Comp. #5
| BOOL | 42.06 | Carrier Chiller Comp. #6
| BOOL | 44.01 | Small Tower Auto Control
| BOOL | 45.04 | LSHH1
| BOOL | 45.05 | LSH1
| BOOL | 45.06 | LSH2
| BOOL | 45.07 | FAULT
| BOOL | 45.08 | Flow Pulse
| BOOL | 50.01 | Open Valve Large Amount
| BOOL | 50.02 | Close Valve Small Amount
| BOOL | 50.03 | Close Valve Large Amount
| BOOL | 50.06 | TEST BIT for Alternate Control
AV51_0010 | CHANNEL | 101 | CC1 Bypass Valve
| CHANNEL | 103 | Output to regen fan (speed)
| CHANNEL | 105 | Output to AV51-2 (steam)
| CHANNEL | 111 | Fine Grinder Flow
| CHANNEL | 113 | CoMill Flow
_1MINUS2_eastLESSTHANTarget | BOOL | 120.01 | East dryer 1st & 2nd flow rate less than Target 20 l/m
_1MINUS2_westLESSTHANTarget | BOOL | 120.02 | West dryer 1st & 2nd flow rate less than Target 12l/m
_3rd_eastLESSTHANTarget | BOOL | 120.03 | East dryer 3rd flow rate less than Target 21 l/m
_3rd_westLESSTHANTarget | BOOL | 120.04 | West dryer 3rd flow rate less than Target 10.5l/m
_4th_eastLESSTHANTarget | BOOL | 120.05 | East dryer 4th flow rate less than Target 19 l/m
_4th_westLESSTHANTarget | BOOL | 120.06 | West dryer 4th flow rate less than Target 8.5l/m
| BOOL | 120.07 | CIP in Step #1 - 1st rinse
| BOOL | 120.08 | CIP in Step #2 (1st Rinse cont'd)
| BOOL | 120.09 | CIP in Step #3 (caustic)
| BOOL | 120.11 | CIP in Step #5 (acid)
| BOOL | 120.12 | CIP in Step #6
| BOOL | 120.13 | CIP Flow < 200 l/m
| CHANNEL | 171 | SPARE INPUT (39,40,41)
T51_5 | CHANNEL | 180 | Stack Temp
T52_48 | CHANNEL | 182 | Small Cooling Tower Outlet
RH51_1 | CHANNEL | 186 | Outside R/H
T51_3 | CHANNEL | 187 | IDH Outlet Temp
T51_5 | CHANNEL | 188 | Regen Fan Stack Temp
T51_1 | CHANNEL | 191 | Air Temp After CC1
T51_2 | CHANNEL | 192 | Temp Before Dessicant Wheel
T51_4 | CHANNEL | 193 | Outside Air Temp
T51_6 | CHANNEL | 194 | Temp After Dessicant Wheel
T51_10 | CHANNEL | 195 | Chiller Outlet Temp
| CHANNEL | 197 | T51-12 RAW
EQUALS | BOOL | 255.06 | System Equals (EQ) Flag
LESS_THAN | BOOL | 255.07 | System Less Than (LE) Flag
| BOOL | 500.03 | Chem. not in CIP
| BOOL | 500.04 | Chem. Park Position
| BOOL | 500.06 | 7/40 Mesh_Sel
| BOOL | 500.07 | 8/40 Mesh_Sel
| BOOL | 500.08 | 20 Mesh_Sel
| BOOL | 500.09 | 40 Mesh_Sel
| BOOL | 500.14 | Chem. Oscillating
| BOOL | 501.01 | 8/40 Mesh Indication
| BOOL | 501.02 | 20 Mesh Indication
| BOOL | 501.03 | 40 Mesh Indication
| BOOL | 501.05 | 40/8 Mesh_Sel
| BOOL | 501.07 | 40/8 Mesh Indication
| BOOL | 501.08 | 8/20 Mesh_Sel
| BOOL | 501.11 | Sterilizer Ozone ALM SCADA
| BOOL | 501.12 | Walter Special
| BOOL | 501.14 | Walter Mesh Indication
| BOOL | 501.15 | Sterilizer Ozone Trouble SCADA
| BOOL | 502.03 | Regrind_Sel
| BOOL | 502.05 | Regrinding Indication
| BOOL | 503.01 | SATAKE LSH1
| BOOL | 503.02 | SATAKE LSH2
| BOOL | 503.03 | SATAKE FAULT
| BOOL | 503.04 | SATAKE ALARM SILENCE SCADA P.B.
| BOOL | 503.05 | SATAKE BUZZER/LIGHT
| BOOL | 503.06 | SCADA RESET P.B.
| BOOL | 503.07 | STOP COMIL TO SCADA
| BOOL | 503.08 | COUNTER STOP SCADA P.B.
| BOOL | 503.11 | COUNTER STOP
| BOOL | 503.12 | BYPASS MODE
| BOOL | 503.13 | BYPASS ENABLED WITHOUT ALARM
| BOOL | 120.10 | CIP in Step #4 (2nd rinse)
| BOOL | 39.00 | Low Speed Contact
| BOOL | 39.10 | Butterfly #3 (N/O) to 7M
| BOOL | 50.00 | Open Valve Small Amount
| BOOL | 501.00 | 7/40 Mesh Indication
| BOOL | 501.10 | 8/20 Mesh Indication
| BOOL | 502.00 | Chiller Not Running Alarm
| BOOL | 503.00 | SATAKE LSHH1
| BOOL | 503.10 | ALARM SILENCE
| BOOL | 51.00 | Reset 5 Minute Counter
| BOOL | CNT052 | Update Timer/Counter
CNT061_PV | UINT | CNT061
| CHANNEL | DM130 | Temperature S.P.
| CHANNEL | DM150 | Glycol Setpoint
| CHANNEL | DM256 | DM257
STER_CIP_STEPS | CHANNEL | DM910 | STERILIZER CIP SEQUENCE TO SET P117 P66 SPEED
East_flow | CHANNEL | DM920 | New Dryer flow rate
EAST_FLOW_RATE | CHANNEL | DM1727 | EAST DRYER FLOW RATE 0-500 Chemetator flow
WEST_FLOW_RATE | CHANNEL | DM1737 | WEST DRYER FLOW RATE 0-130 l/m
| CHANNEL | DM1747 | Regen Fan Amps
| CHANNEL | DM1767 | Main Fan Amps
| CHANNEL | DM2750 | 51-3 SET POINT result
| CHANNEL | DM2800 | C (S.P.)
| CHANNEL | DM2801 | C+1 (Prop.)
| CHANNEL | DM2802 | C+2 (Int.)
| CHANNEL | DM2803 | C+3 (Deriv.)
| CHANNEL | DM2804 | C+4 (Sample)
| CHANNEL | DM2805 | C+5 (FWD/REV*)
| CHANNEL | DM2806 | C+6 (IN Range ¦ Time ¦ OUT Range)
| CHANNEL | DM3499 | P66 SCADA SPEED SETPOINT
P66_SP | CHANNEL | DM3500 | P66 SPEED SETPOINT
P117_SP | CHANNEL | DM3501 | P117 SPEED SETPOINT
| CHANNEL | DM5200 | High Deadband Limit
| CHANNEL | DM5201 | High High DeadBand Limit
| CHANNEL | DM5202 | Low DeadBand Limit
| CHANNEL | DM5203 | Low Low DeadBand Limit
| CHANNEL | DM5209 | IDH Outlet Temperature Scaled
| CHANNEL | DM5210 | Previous CC3 Output
| CHANNEL | DM5211 | Current CC3 Output
| CHANNEL | DM5212 | HEX Output
| CHANNEL | DM5213 | Scaled Hex Output
| CHANNEL | DM5215 | IDH Outlet Setpoint
| CHANNEL | DM5217 | Physical Output (104)
| CHANNEL | DM5221 | T51-12 SCALED
| BOOL | HR1.05 | CC3 Summer Operation
| BOOL | HR1.06 | T51-12 Auto/Man (0=M : 1=A)
| BOOL | HR1.07 | CC3 Winter Operation
| BOOL | HR1.08 | T51-12 Summer/Winter (0=S : 1=W)
| BOOL | HR2.04 | Temp. < Low Speed Setpoint
| BOOL | HR2.05 | Temp. > Low Speed Setpoint
| BOOL | HR2.06 | Low Speed Start/Stop
| BOOL | HR2.07 | Temp. < Hi Speed Setpoint
| BOOL | HR2.08 | Temp. > Hi Speed Setpoint
| BOOL | HR2.09 | Hi Speed Start/Stop
| BOOL | TIM062 | ALARM SILENCE RESET TIMER
| BOOL | TIM063 | RESET P.B. RESET TIMER
| BOOL | TIM064 | COUNTER STOP RESET TIMER
| BOOL | TIM065 | ALARM SILENCE TIMER
| BOOL | TIM066 | STOP COMIL DELAY
| BOOL | TIM068 | Ozone Leak Delay
| BOOL | TIM069 | Ozone Trouble Delay

## CrossRef
Address | Input | Output | Description
0.00 |  | a0266
0.01 |  | a0286
0.02 |  | a0270
0.03 |  | a0290
0.04 |  | a0274
0.05 |  | a0294
0.06 |  | a0278
0.07 |  | a0298
0.08 |  | a0282
0.09 |  | a0302
1.00 | a0366 | a0365
1.01 | a0379 | a0378
100 |  | 0322
101 | 0470, 0473, 0807, 0810 |  | CC1 Bypass Valve
102 |  | 0488, 0491
103 |  | 0505, 0508 | Output to regen fan (speed)
104 | 0524, 0527, 0575, 0662, 0828
105 |  | 0698, 0708, 0725, 0727, 0732, 0739, 0743, 0746 | Output to AV51-2 (steam)
11.00 | a0853
11.01 | a0855
11.02 | a0857
11.04 | a0884 |  | Feed back from Sterilizer PLC CIP step to change P
11.05 | b1200 |  | Sterilizer Ozone ALM
11.06 | b1204 |  | Sterilizer Ozone Trouble ALM
110 |  | 0323
111 |  | 0424, 0426 | Fine Grinder Flow
112 |  | 0430
113 |  | 0434, 0450 | CoMill Flow
120.01 | a0142, a0157 |  | East dryer 1st & 2nd flow rate less than Target 20 l/m
120.02 | a0146, a0161 |  | West dryer 1st & 2nd flow rate less than Target 12 l/m
120.03 |  | a0172 | East dryer 3rd flow rate less than Target 21 l/m
120.04 |  | a0176 | West dryer 3rd flow rate less than Target 10.5 l/m
120.05 |  | a0187 | East dryer 4th flow rate less than Target 19 l/m
120.06 |  | a0191 | West dryer 4th flow rate less than Target 8.5 l/m
120.07 | a0868 | a0921, b0931 | CIP in Step #1 - 1st rinse
120.08 | a0880 | a0922, b0932 | CIP in Step #2 (1st Rinse cont'd)
120.09 | a0888 | a0923, b0933 | CIP in Step #3 (caustic)
120.10 | a0900 | a0924, b0934 | CIP in Step #4 (2nd rinse)
120.11 | a0912 | a0925, b0935 | CIP in Step #5 (acid)
120.12 | a0918 | a0926, b0936 | CIP in Step #6
120.13 |  | a0930 | CIP Flow < 200 l/m
130 |  | 0324
170 |  | 0325
171 | 0335 |  | SPARE INPUT (39,40,41)
172 | 0339, 0346, 0348, 0350, 0354
172.15 | a0341
173 | 0371
173.15 | a0373
174 | 0384, 0387
175 | 0390
176 | 0393
177 | 0396
178 | 0399
180 | 0326 |  | Stack Temp
181 | 0329
182 | 0748 |  | Small Cooling Tower Outlet
185 | 0332
186 | 0333 |  | Outside R/H
187 | 0524, 0529, 0579, 0585, 0684, 0807, 0812, 0823 |  | IDH Outlet Temp
188 | 0356, 0505, 0510 |  | Regen Fan Stack Temp
190 | 0327
191 | 0330, 0470, 0475, 0583 |  | Air Temp After CC1
192 | 0488, 0493, 0581 |  | Temp Before Desiccant Wheel
193 | 1214 |  | Outside Air Temp
194 | 0577 |  | Temp After Desiccant Wheel
195 | 1225 |  | Chiller Outlet Temp
197 | 0674, 0687, 0693 |  | TS1-12 RAW
232.03 | a0136 | b0200, a0253
232.04 | a0151 | b0201, a0255
232.05 | a0166 | b0202, a0257
232.06 | a0181 | b0203, a0259
232.07 | a0195 | b0204, a0261
232.08 | a0205, a0208, b0213, b0217, b0219, a0221, b0223, b0228, b0233, b0238, b0243, b0250
253.13 |  |  | Always ON Flag
253.14 |  |  | Always OFF Flag
253.15 | a0011, b0017, b0129, a0307, a0309, a0311, a0313, a0315, a0317, a0319, a0321, a0815 |  | First Cycle Flag
254.00 | a0817, b0844, a1242 |  | 1 minute clock pulse bit
255.02 | a0360, a0460, a0478, a0496, a0513, a0625, a0669, a0711, a0940 |  | 1.0 second clock pulse bit
255.03 | a0556 |  | Instruction Execution Error (ER) Flag
255.04 | a0508 |  | Carry (CY) Flag
255.05 |  |  | Greater Than (GT) Flag
255.06 | a0045, b0058, b0063, b0068, b0072, b0085, b0088, a0095, b0098, a0110, a0128, a0150, a0170, a0190, a0193, b0196, b0198, a0203, a0206, b0212, a0227 |  | System Equals (EQ) Flag
255.07 | b0008, b0010, b0028, a0141, a0145, a0156, a0160, a0171, a0175, a0185, a0190, a0351, a0364, a0377, a0427, a0431, a0451, a0562, a0614, a0620, a0656, a0673, a0723, a0745, a0759, a0789, a0824, a0829, a0847, a0928 |  | System Less Than (LE) Flag
289.08 | a0000, a0036, b0080, b0128
300.00 | b0649, a0472 | a0477
300.01 | b0487, a0490 | a0495
300.02 | b0504, a0507 | a0512
300.03 | b0523, a0526 | a0531
300.04 |  | a0691
300.05 | b0806, a0809 | a0814
300.06 | a0689 | a0695
300.09 | a0842 | a0841
300.10 | a0820 | a0843
300.11 |  | a0825
39.00 | a0780, b0800 |  | Low Speed Contact
39.01 | a0801, b0778 |  | Hi Speed Contact
39.06 | a0369
39.07 | a0382
39.08 | a0959, a0977, a0986, a1006, a1026, a1046, a1072, a1101, a1159, a1179 |  | Butterfly #1 (N/C) to F/G
39.09 | a0989, a1007, a1027, a1047, a1077, a1082, a1118, a1160, a1181 |  | Butterfly #2 (N/O) to 7M
39.10 | a0988, a1008, a1028, a1048, a1074, a1124, a1130, a1161, a1182 |  | Butterfly #3 (N/O) to 7M
39.11 | a0960, a0974, a0981, a1009, a1029, a1049, a1073, a1102, a1162, a1180 |  | Butterfly #4 (N/C) to F/G
39.12 |  | a1197
39.13 |  | a1199
39.14 |  | a1289
39.15 |  | a0459
40.00 | b0407, b0410, b0418, b0421 | a0196
42.01 |  | b1208, b1219 | Carrier Chiller Comp. #1
42.02 |  | b1209, b1220 | Carrier Chiller Comp. #2
42.03 |  | b1210, b1221 | Carrier Chiller Comp. #3
42.04 |  | b1211, b1222 | Carrier Chiller Comp. #4
42.05 |  | b1212, b1223 | Carrier Chiller Comp. #5
42.06 |  | b1213, b1224 | Carrier Chiller Comp. #6
44.01 | a0749, a0757, a0763, a0776, a0781, a0787, a0798 |  | Small Tower Auto Control
44.04 |  | a0303
44.05 |  | a0305
45.04 | a1233, a1262, a1276, b1282 |  | LSHH1
45.05 | a1235, a1241, a1245, a1261, a1277, b1283 |  | LSH1
45.06 | a1237, a1278, b1284 |  | LSH2
45.07 | a1239, a1279, b1285 |  | FAULT
45.08 | a0947 |  | Flow Pulse
50.00 | a0641 | a0603 | Open Valve Small Amount
50.01 | b0642, a0645 | a0609 | Open Valve Large Amount
50.02 | a0637 | a0615 | Close Valve Small Amount
50.03 | a0634, b0638 | a0621 | Close Valve Large Amount
50.06 | b0552, b0569, b0571, a0587, a0591, a0599, a0605, a0611, a0617, a0622, a0626, a0629, a0647, a0659 |  | TEST BIT for Alternate Control
50.07 | a0675, a0683 |  | Reset 5 Minute Counter
500.00 |  | a0854
500.01 |  | a0856
500.02 |  | a0858
500.03 | a0938, b0941, a0944 | a0937 | Chem. not in CIP
500.04 | a0949 | a0948, a0952 | Chem. Park Position
500.05
500.06 | a0955 | a0961 | 7/40 Mesh_Sel
500.07 | a0999 | a1003 | 8/40 Mesh_Sel
500.08 | a1039 | a1043 | 20 Mesh_Sel
500.09 | a1059 | a1063 | 40 Mesh_Sel
500.10 | a0957 | a0956
500.11 | a1001 | a1000
500.12 | a1041 | a1040
500.13 | a1061 | a1060
500.14 |  | a0946 | Chem. Oscillating
501.00 | a0963 | a0958, a1010, a1030, a1050, a1084, a1132, a1163, a1183 | 7/40 Mesh Indication
501.01 | a1005 | a0990, a1002, a1031, a1051, a1085, a1133, a1164, a1184 | 8/40 Mesh Indication
501.02 | a1045 | a0992, a1012, a1032, a1042, a1087, a1135, a1165, a1185 | 20 Mesh Indication
501.03 | a1044, a1065 | a0993, a1013, a1033, a1053, a1062, a1136, a1166, a1186 | 40 Mesh Indication
501.04 |  | a1046, b1075, a1079, b1106, a1115, a1122, b1128
501.05 | a1093 | a1097 | 40/8 Mesh_Sel
501.06 | a1095 | a1094
501.07 | a1043, a1099 | a0994, a1014, a1034, a1054, a1088, a1096, a1167, a1187 | 40/8 Mesh Indication
501.08 | a1019 | a1023 | 8/20 Mesh_Sel
501.09 | a1021 | a1020
501.10 | a0991, a1011, a1022, a1052, a1086, a1134, a1168, a1188 | a1025 | 8/20 Mesh Indication
501.11 | a1203 |  | Sterilizer Ozone ALM SCADA
501.12 | a1152 | a1156 | Walter Special
501.13 | a1154 | a1153
501.14 | a0995, a1015, a1035, a1055, a1089, a1137, a1155, a1189 | a1158 | Walter Mesh Indication
501.15 | a1207 |  | Sterilizer Ozone Trouble SCADA
502.00 | a1218 | a1230 | Chiller Not Running Alarm
502.01 | a1229 | a1232
502.02 | a1231
502.03 | a1176 | a1172 | Regrind_Sel
502.04 | a1173 | a1174
502.05 | a0996, a1016, a1036, a1056, a1090, a1138, a1169, a1175 | a1178 | Regrinding Indication
503.00 | a1234 |  | SATAKE LSHH1
503.01 | a1236 |  | SATAKE LSH1
503.02 | a1238 |  | SATAKE LSH2
503.03 | a1240 |  | SATAKE FAULT
503.04 | a1271 | a1267 | SATAKE ALARM SILENCE SCADA P.B.
503.05 | a1281 | a1288 | SATAKE BUZZER/LIGHT
503.06 | a1255 | a1244, a1252 | SCADA RESET P.B.
503.07 | a1266 |  | STOP COMIL TO SCADA
503.08 | a1260 | a1255 | COUNTER STOP SCADA P.B.
503.10 | a1269, a1275, a1272, b1280 |  | ALARM SILENCE
503.11 | a1249, a1258 | b1243 | COUNTER STOP
503.12 | a1263, a1286 |  | BYPASS MODE
503.13 | a1287 |  | BYPASS ENABLED WITHOUT ALARM
51.00 | a0664, a0627
60.00 |  | a0762
60.01 | a0770, b0774
60.02 | a0793 | a0786
91.00 | b0048 | a0075
91.01 | b0009, b0016, a0023, a0047, b0055 | a0049, a0069, a0073
91.03 | b0079, a0127
92.00 | b0010, a0015 | a0002
AR01.00 | a0308
AR01.01 |  | a0310
AR01.02 |  | a0312
AR01.03 |  | a0314
AR01.07 |  | a0316
AR01.08 |  | a0318
AR01.09 |  | a0320
b0830
CNT020 | a0214, a0212, a0216
CNT030 |  | a0218
CNT031(bit) | a0821, a0826
CNT041(bit) | a0628, a0632, a0663
CNT051(bit) | a0943, a0942
CNT052(bit) | a0718, a0716, a0721, a0735 |  | Update Timer/Counter
CNT061 | 1251
CNT061(bit) |  | a1247 | COUNTER TO STOP COMIL
DM0 |  | 0137
DM1 |  | 0138
DM10 | 1251
DM100 | 0462
DM102 | 0462, 0463
DM104 | 0463, 0467
DM106 | 0467, 0468
DM110 | 0480
DM112 | 0480, 0481
DM1121 | 0424
DM1122 | 0430
DM1123 | 0450
DM114 | 0481, 0485
DM116 | 0485, 0486
DM1170 | 0335
DM1171 | 0335, 0336
DM120 | 0498
DM122 | 0498, 0499
DM124 | 0499, 0502
DM126 | 0502, 0503
DM130 | 0515 |  | Temperature S.P.
DM132 | 0515, 0516
DM134 | 0516, 0521, 0533, 0804
DM136 | 0521, 0522, 0533, 0804, 0805, 0823
DM140 | 0671, 0839
DM141 | 0698
DM142 | 0671, 0672
DM144 | 672
DM147 | 701
DM148 | 0704, 0718
DM149 | 684
DM150 | 0816, 0831, 0836, 0839, 0846, 0848, 0850, 0852 |  | Glycol Setpoint
DM1712 | 0336
DM1717 | 0336
DM1720 | 0339
DM1721 | 0339, 0340
DM1722 | 0340
DM1727 | 0140, 0155, 0170, 0185, 0340, 0342, 0344, 0363, 0402, 0927 |  | EAST DRYER FLOW RATE 0-500, Chemetator flow
DM1728 | 0402, 0408
DM1730 | 0371
DM1731 | 0371, 0372
DM1732 | 0372
DM1737 | 0144, 0159, 0174, 0189, 0372, 0374, 0376, 0413 |  | WEST DRYER FLOW RATE 0-130 l/m
DM1738 | 0413, 0419
DM1740 | 0384
DM1741 | 0384, 0385, 0387, 0388
DM1742 | 0385, 0388
DM1747 | 0385, 0388 |  | Regen Fan Amps
DM1750 | 0390
DM1751 | 0390, 0391
DM1752 | 0391
DM1757 | 0391
DM1760 | 0393
DM1761 | 0393, 0394
DM1762 | 0394
DM1767 | 0394 |  | Main Fan Amps
DM1770 | 0396
DM1771 | 0396, 0397
DM1772 | 0397
DM1777 | 0397
DM1780 | 0399
DM1781 | 0399, 0400
DM1782 | 0400
DM1787 | 0400
DM1790 | 0332
DM180 | 0346
DM1821 | 0329
DM184 | 0346
DM1886 | 0333
DM1921 | 0330
DM2 |  | 0152
DM200 | 0354
DM204 | 0354, 0358
DM215 | 0358, 0361
DM217 | 0361, 0361
DM220 | 0539, 0543, 0543, 0554
DM221 | 0545, 0545
DM222 | 0546, 0546
DM223 | 0547, 0547
DM224 | 0548, 0548
DM225 | 0549
DM226 | 0550
DM24 | 1191
DM25 | 1068, 1191
DM255 | 0535
DM256 | 0535, 0536
DM257 | 0536, 0537
DM258 | 0537, 0538
DM259 | 0538, 0539
DM260 | 0554, 0561, 0563, 0565, 0567, 0570, 0575
DM2600 | 0468, 0470
DM261 | 0570
DM2650 | 0486, 0488
DM27 | 1192
DM270 | 0579
DM2700 | 0503, 0505
DM274 | 0554, 0579, 0722, 0736
DM275 | 0581
DM2750 | 0522, 0524 | 51-3 SET POINT result
DM279 | 0581
DM28 | 1070, 1192
DM280 | 0583
DM2800 | 0676, 0684 | C (S.P.)
DM2801 | 0677 | C+1 (Prop.)
DM2802 | 0678 | C+2 (Int.)
DM2803 | 0679 | C+3 (Deriv.)
DM2804 | 0680 | C+4 (Sample)
DM2805 | 0681 | C+5 (FWD/REV)
DM2806 | 0682 | C+6 (IN Range | Time
DM284 | 0583
DM285 | 0577
DM2850 | 0805, 0807
DM289 | 0577
DM3 |  | 0153
DM30 | 1194
DM300 | 0748
DM3000 | 0033, 0044, 0082, 0084, 0095, 0106, 0117
DM3001 | 0034, 0082
DM3002 | 0035, 0082
DM3005 | 0002, 0004, 0006, 0007, 0012, 0017, 0019, 0024, 0027, 0029, 0030, 0040
DM3006 | 0004, 0013, 0020, 0025, 0030, 0034
DM3007 | 0006, 0014, 0021, 0026, 0031, 0035
DM3008 | 0040, 0041
DM3009 | 0041
DM304 | 0748, 0750, 0758, 0764, 0782, 0788
DM31 | 1146, 1194
DM310 | 0356
DM314 | 0356
DM3143 | 0077
DM3148 | 0078
DM33 | 1195
DM34 | 1149, 1195
DM3499 | 0864, 0874, 0878, 0896, 0906, 0916, 0920 |  | P66 SCADA SPEED SETPOINT
DM3500 | 0050, 0052, 0060, 0067, 0077, 0864, 0874, 0878, 0896, 0906, 0910, 0916 | P66 SPEED SETPOINT
DM3501 | 0051, 0053, 0065, 0078, 0865, 0873, 0879, 0887, 0895, 0905, 0911, 0917 | P117 SPEED SETPOINT
DM3505 | 0052, 0057, 0059
DM3506 | 0053, 0062, 0064
DM3521 | 0050, 0057, 0059, 0060, 0067
DM3526 | 0051, 0062, 0064, 0065, 0071
DM3553 | 0086, 0088, 0097, 0099
DM3558 | 0089, 0100
DM3563 | 0090, 0101
DM3568 | 0091, 0102
DM3573 | 0092, 0103
DM3578 | 0093, 0104
DM3603 | 0108, 0110, 0119, 0121
DM3608 | 0111, 0122
DM3613 | 0112, 0123
DM3618 | 0113, 0124
DM3623 | 0114, 0125
DM3628 | 0115, 0126
DM3800 | 0088, 0099
DM3801 | 0089, 0100
DM3802 | 0090, 0101
DM3803 | 0091, 0102
DM3804 | 0092, 0103
DM3805 | 0093, 0104
DM3806 | 0110, 0121
DM3807 | 0111, 0122
DM3808 | 0112, 0123
DM3809 | 0113, 0124
DM3810 | 0114, 0125
DM3811 | 0115, 0126
DM4 |  | 0167
DM4000 | 0130
DM4005 | 0130
DM5 |  | 0168
DM500 | 0220, 0224
DM501 | 0222, 0226
DM502 | 0224, 0225
DM503 | 0225, 0229
DM505 | 0226, 0227
DM506 | 0227, 0229
DM508 | 0229, 0230
DM509 | 0230, 0234, 0235, 0236, 0237, 0239, 0240, 0241, 0242
DM510 | 0231
DM511 | 0234, 0235, 0236, 0237, 0239, 0240, 0241, 0242, 0244, 0245, 0246, 0247, 0248, 0249, 0251, 0252
DM512 | 0254, 0256, 0258, 0260, 0262
DM513 | 0231, 0232
DM515 | 0232, 0244, 0245, 0246, 0247, 0248, 0249, 0251, 0252
DM5200 | 0600, 0601 |  | High Deadband Limit
DM5201 | 0606, 0607 |  | High High Deadband Limit
DM5202 | 0612, 0613 |  | Low Deadband Limit
DM5203 | 0618, 0619 |  | Low Low Deadband Limit
DM5204 | 0585, 0586
DM5205 | 0586
DM5209 | 0586, 0601, 0607, 0613, 0619 |  | IDH Outlet Temperature Scaled
DM5209 | 0586, 0601, 0607, 0613, 0619 |  | IDH Outlet Temperature Scaled
DM5210 | 0590, 0667 |  | Previous CC3 Output
DM5210 | 0590, 0667 |  | Previous CC3 Output
DM5211 | 0590, 0594, 0597, 0635, 0636, 0639, 0643, 0646, 0651, 0653, 0655, 0657, 0660, 0667 |  | Current CC3 Output
DM5211 | 0590, 0594, 0597, 0635, 0636, 0639, 0643, 0646, 0651, 0653, 0655, 0657, 0660, 0667 |  | Current CC3 Output
DM5212 | 0660, 0661 |  | HEX Output
DM5212 | 0660, 0661 |  | HEX Output
DM5213 | 0661, 0662 |  | Scaled Hex Output
DM5213 | 0661, 0662 |  | Scaled Hex Output
DM5215 | 0600, 0606, 0612, 0618 |  | IDH Outlet Setpoint
DM5215 | 0600, 0606, 0612, 0618 |  | IDH Outlet Setpoint
DM5217 | 0674 |  | Physical Output (104)
DM5217 | 0674 |  | Physical Output (104)
DM5221 | 0674 |  | T51-12 SCALED
DM5221 | 0674 |  | T51-12 SCALED
DM6 |  | 0182
DM7 |  | 0183
DM8 | 0197
DM800 | 0405, 0408
DM801 | 0416, 0419
DM9 | 0198
DM900 | 0137, 0152, 0167, 0182, 0197, 0405
DM901 | 0138, 0153, 0168, 0183, 0198, 0416
DM902 | 0139, 0154, 0169, 0184, 0199, 0264, 0268, 0272, 0276, 0280, 0284, 0288, 0292, 0296, 0300
DM910 | 0860, 0870, 0876, 0882, 0890, 0902, 0908, 0914 |  | STERILIZER CIP SEQUENCE TO SET P117 P66 SPEED
DM920 | 0344 |  | New Dryer flow rate
DM930 | 0434
DM934 | 0434
DM935 | 0426
DM939 | 0426, 0436
HR01.00 | a0304, a0263, a0267, a0271, a0275, a0279
HR01.01 | a0306
HR01.02 | a0464
HR01.03 | a0482
HR01.04 | a0500
HR01.05 | a0518, a0588, b0592, b0595, a0623, a0630, a0648, a0665 |  | CC3 Summer Operation
HR01.06 | b0696, b0699, b0702, b0705, a0706, a0709, b0712, a0714, a0719, a0733 |  | T51-12 Auto/Man (0=M : 1=A)
HR01.07 | b0645, b0483, b0519, b0589, b0593, b0596, b0624, b0631, b0649, b0666, b0802 |  | CC3 Winter Operation
HR01.08 | a0697, a0700, a0703, a0707, a0710, b0713, a0715, a0720, a0734 |  | T51-12 Summer/Winter (O=S : 1=W)
HR01.09 | a0540, a0551, b0568, b0572, a0573
HR01.10 | a0556
HR01.11 |  | a0559
HR02.00 | a0411, a0453
HR02.01 | a0422, a0454
HR02.02 | a0456
HR02.03 | a0455
HR02.04 | a0768, a0773 |  | Temp. < Low Speed Setpoint
HR02.05 | a0771, a0772 |  | Temp. > Low Speed Setpoint
HR02.06 | a0775, a0777 |  | Low Speed Start/Stop
HR02.07 | a0792, a0796 |  | Temp. < Hi Speed Setpoint
HR02.08 | a0794, a0795 |  | Temp. > Hi Speed Setpoint
HR02.09 | a0797, b0779, a0799 |  | Hi Speed Start/Stop
HR02.10 | a0428
HR02.11 | a0432
HR02.12 | a0452
HR03.00 | a0457
HR03.01 | a0458
HR10.00 | a0131, b0147, a0162, b0177, a0192
HR10.01 | b0132, a0148, a0163, b0178, b0193
HR10.02 | b0133, b0149, b0164, a0179, a0194
HR10.03 | b0134
TIM000(bit) | a0037, a0038
TIM005(bit) | a0867, b0863, a0872
TIM006(bit) | a0899, b0893, a0904
TIM010(bit) | a0209, b0207, a0211
TIM015(bit) | a0367, a0368
TIM016(bit) | a0380, a0381
TIM017(bit) | a0929
TIM021(bit) | a0754, a0755
TIM022(bit) | a0760, a0761
TIM023(bit) | a0766, a0767
TIM024(bit) | a0784, a0785
TIM025(bit) | a0790, a0791
TIM026(bit) | a1068, b1076, a1080
TIM027(bit) | a1070, b1067
TIM028(bit) | a0440, a0441
TIM029(bit) | a0967, a0968, a0984
TIM032(bit) | a0982, b0965, b0980
TIM033(bit) | a0969, b0973, a0979
TIM034(bit) | a0971, a0976, b0985
TIM035(bit) | a0448, a0445
TIM036(bit) | a1140, b1104, a1113, a1142
TIM037(bit) | a1143, b1139
TIM038(bit) | a1146, b1121, a1127, a1148
TIM039(bit) | a1149, b1145
TIM060(bit) | a0950, a0951
TIM062(bit) | a1268, a1270 |  | ALARM SILENCE RESET TIMER
TIM063(bit) | a1253, a1254 |  | RESET P.B. RESET TIMER
TIM064(bit) | a1257, a1259 |  | COUNTER STOP RESET TIMER
TIM065(bit) | a1273, a1274 |  | ALARM SILENCE TIMER
TIM066(bit) | a1264, a1265 |  | STOP COMIL DELAY
TIM068(bit) | a1201, a1202 |  | Ozone Leak Delay
TIM069(bit) | a1205, a1206 |  | Ozone Trouble Delay

## SCADA_Tags
Symbol | Type | Address | Description
IDH_SATAKE_BYPASS_REMINDER | DA | IR503.13 | SATAKE Bypass Enabled with No Alarms Present
DRIER_FLOW_STPT_EAST_1ST_AI | AI | DM0@bcd
IDH_SATAKE_COUNTER_PV | AI | DM10@BCD | SATAKE Counter Value
T51-1_SETPT_AI | AI | DM100
T51-1_SETPT_AR | AI | DM100 | (NGC)
T51-1_SETPT_AO | AO | DM100
T51-1_STPT | AA | DM100
T51-2_STPT_AI | AI | DM110
T51-2_STPT_AR | AI | DM110 | (NGC)
T51-2_STPT_AO | AO | DM110
T51-2_STPT | AA | DM110
T51-5_STPT_AI | AI | DM120
T51-5_STPT_AR | AI | DM120 | (NGC)
T51-5_STPT_AO | AO | DM120
T51-5_STPT | AA | DM120
T51-3_STPT_AI | AI | DM130
T51-3_STPT_AR | AI | DM130 | (NGC)
T51-3_STPT_AO | AO | DM130
T51-3_STPT | AA | DM130
T51-12_STPT_AI | AI | DM140
T51-12_STPT_AR | AI | DM140 | (NGC)
T51-12_STPT_AO | AO | DM140
T51-12_MAN_OUTPUT | AO | DM141 | T51-12 MANUAL OUTPUT (AV51-2)
CFM_51-1 | AA | DM1717 | IDH AIR FLOW
DRIER_FLOW_CIP_EAST | AA | DM1727 | CIP EAST DRIER FLOWRATE
DRIER_FLOW_4TH_EAST | AA | DM1727 | 4TH COOK EAST DRIER FLOWRATE
DRIER_FLOW_3RD_EAST | AA | DM1727 | 3RD COOK EAST DRIER FLOWRATE
DRIER_FLOW_2ND_EAST | AA | DM1727 | 2ND COOK EAST DRIER FLOWRATE
DRIER_FLOW_1ST_EAST | AA | DM1727 | 1ST COOK EAST DRIER FLOWRATE
DRIER_EAST_FLOW_REP1 | AA | DM1727 | USED FOR SLOWDOWN REPORT
DRIER_EAST_FLOW_REP | AA | DM1727 | USED FOR SLOWDOWN REPORT
EAST_DRIER_FLOW | AA | DM1727 | EAST DRIER FLOWRATE
IDH_REGEN_FAN_AMPS | AA | DM1747@BCD | IDH REGEN FAN AMPS
DEW_51-1_RAW | AA | DM1757
IDH_MAIN_FAN_AMPS | AA | DM1767@BCD | IDH main fan amps
L52-51 | AA | DM1790 | Chiller Tank lvl high or low
DRIER_FLOW_STPT_EAST_2ND_AI | AI | DM2@bcd
CHEM_TEST_FLOW_AVG_1 | AA | DM210 | CHEMETATOR FLOW AVG (minute)
CHEM_TEST_FLOW_AVG_2 | AA | DM213 | CHEMETATOR FLOW AVG (hour)
IDH_T51-3_PROPORTIONAL | AI | DM221@BCD | T51-3 PROPORTIONAL
IDH_T51-3_INTEGRAL | AI | DM222@BCD | T51-3 INTEGRAL
IDH_T51-3_DERIVATIVE | AI | DM223@BCD | T51-3 DERIVATIVE
IDH_T51-3_SAMPLE | AI | DM224 | T51-3 SAMPLE PERIOD
IDH_40M_VALVE_TIME_OFF | AI | DM24@BCD | V2 Closed Time (minutes)
IDH_T51-3_SETPOINT | AA | DM255@BCD | T51-3 SETPOINT
IDH_T51-3_OUTPUT | AI | DM260 | T51-3 OUTPUT
T-51-1_PROPORTIONAL | AI | DM2601 | (NGC)
T-51-1_PROPORTIONAL_AI | AI | DM2601
T-51-1_PROPORTIONAL_AO | AO | DM2601
T51-1_INTEGRAL | AI | DM2602 | (NGC)
T51-1_INTEGRAL_AI | AI | DM2602
T51-1_INTEGRAL_AO | AO | DM2602
T51-1_DERIVATIVE | AI | DM2603 | (NGC)
T51-1_DERIVATIVE_AI | AI | DM2603
T51-1_DERIVATIVE_AO | AO | DM2603
T51-1_SAMPLING | AI | DM2604 | (NGC)
T51-1_SAMPLING_AI | AI | DM2604
T51-1_SAMPLING_AO | AO | DM2604
T51-2_PROPORTIONAL | AI | DM2651 | (NGC)
T51-2_PROPORTIONAL_AI | AI | DM2651
T51-2_PROPORTIONAL_AO | AO | DM2651
T51-2_INTEGRAL | AI | DM2652 | (NGC)
T51-2_INTEGRAL_AI | AI | DM2652
T51-2_INTEGRAL_AO | AO | DM2652
T51-2_DERIVATIVE | AI | DM2653 | (NGC)
T51-2_DERIVATIVE_AI | AI | DM2653
T51-2_DERIVATIVE_AO | AO | DM2653
T51-2_SAMPLING | AI | DM2654 | (NGC)
T51-2_SAMPLING_AI | AI | DM2654
T51-2_SAMPLING_AO | AO | DM2654
IDH_40M_VALVE_TIME_ON | AI | DM27@BCD | V2 Open Time (seconds)
T51-5_PROPORTIONAL | AI | DM2701 | (NGC)
T51-5_PROPORTIONAL_AI | AI | DM2701
T51-5_PROPORTIONAL_AO | AO | DM2701
T51-5_INTEGRAL | AI | DM2702 | (NGC)
T51-5_INTEGRAL_AI | AI | DM2702
T51-5_INTEGRAL_AO | AO | DM2702
T51-5_DERIVATIVE | AI | DM2703 | (NGC)
T51-5_DERIVATIVE_AI | AI | DM2703
T51-5_DERIVATIVE_AO | AO | DM2703
T51-5_SAMPLING | AI | DM2704 | (NGC)
T51-5_SAMPLING_AI | AI | DM2704
T51-5_SAMPLING_AO | AO | DM2704
T51-3_SCADA_SCALED | AA | DM274 | DRIER TEMP IN FROM IDH
T51-3_RAW | AA | DM274 | DRIER TEMP IN FROM IDH
T51-3_S_PROPORTIONAL | AI | DM2751 | (NGC)
T51-3_S_PROPORTIONAL_AI | AI | DM2751
T51-3_S_PROPORTIONAL_AO | AO | DM2751
T51-3_S_INTEGRAL | AI | DM2752 | (NGC)
T51-3_S_INTEGRAL_AI | AI | DM2752
T51-3_S_INTEGRAL_AO | AO | DM2752
T51-3_S_DERIVATIVE | AI | DM2753 | (NGC)
T51-3_S_DERIVATIVE_AI | AI | DM2753
T51-3_S_DERIVATIVE_AO | AO | DM2753
T51-3_S_SAMPLING | AI | DM2754 | (NGC)
T51-3_S_SAMPLING_AI | AI | DM2754
T51-3_S_SAMPLING_AO | AO | DM2754
T51-2_SCADA_SCALED | AA | DM279@BCD | Air Temp Before Dessicant Wheel
T51-12_PROPORTIONAL | AI | DM2801 | (NGC)
T51-12_PROPORTIONAL_AI | AI | DM2801
T51-12_PROPORTIONAL_AO | AO | DM2801
T51-12_INTEGRAL | AI | DM2802 | (NGC)
T51-12_INTEGRAL_AI | AI | DM2802
T51-12_INTEGRAL_AO | AO | DM2802
T51-12_DERIVATIVE | AI | DM2803 | (NGC)
T51-12_DERIVATIVE_AI | AI | DM2803
T51-12_DERIVATIVE_AO | AO | DM2803
T51-12_SAMPLING | AI | DM2804 | (NGC)
T51-12_SAMPLING_AI | AI | DM2804
T51-12_SAMPLING_AO | AO | DM2804
T51-1_SCADA_SCALED | AA | DM284@BCD | Air Temp After CC1
T51-3_W_PROPORTIONAL | AI | DM2851 | (NGC)
T51-3_W_PROPORTIONAL_AI | AI | DM2851
T51-3_W_PROPORTIONAL_AO | AO | DM2851
T51-3_W_INTEGRAL | AI | DM2852 | (NGC)
T51-3_W_INTEGRAL_AI | AI | DM2852
T51-3_W_INTEGRAL_AO | AO | DM2852
T51-3_W_DERIVATIVE | AI | DM2853 | (NGC)
T51-3_W_DERIVATIVE_AI | AI | DM2853
T51-3_W_DERIVATIVE_AO | AO | DM2853
T51-3_W_SAMPLING | AI | DM2854 | (NGC)
T51-3_W_SAMPLING_AI | AI | DM2854
T51-3_W_SAMPLING_AO | AO | DM2854
T51-6_SCADA_SCALED | AA | DM289@BCD | After Wheel Temp
IDH_40_7M_VALVE_TIME_ON | AI | DM30@BCD | V3 Open Time (seconds)
T51-5_PV_TO_BURNER_AA | AA | DM314@BCD | IDH regen temp HI or LO
IDH_40_7M_VALVE_TIME_OFF | AI | DM33@BCD | V3 Closed Time (seconds)
STER_P66_SETPOINT | AI | DM3499@BCD | P66 Speed Setpoint
DRI_CONT_P116_SP_AR | AI | DM3500 | (NGC) p116 controller stpt ar
DRI_CONT_P116_SP_AO | AO | DM3500 | p116 controller stpt ao
DRI_CONT_P118_SP_AR | AI | DM3501 | (NGC) p118 controller stpt ar
DRI_CONT_P118_SP_AO | AO | DM3501 | p118 controller stpt ao
STER_P117_SETPOINT | AI | DM3501@BCD | P117 Speed Setpoint
DRI_CONT_P116_PV | AI | DM3511 | P116 CONTROLLER PV
DRI_CONT_P118_PV | AI | DM3516 | P118 CONTROLLER PV
DRI_CONT_P116_SP_AI | AI | DM3521 | p116 controller stpt ai
DRI_CONT_P118_SP_AI | AI | DM3526 | P118 CONTROLLER PV
DRIER_FLOW_STPT_EAST_3RD_AI | AI | DM4@bcd
CC3_TEMPERATURE | AI | DM5209@BCD | IDH Outlet Temperature
CC3_OUTPUT | AI | DM5211@BCD | CC3 Cooling Valve Output
CC3_SETPOINT_AO | AO | DM5215@BCD | CC3 Setpoint Out
DRIER_FLOW_STPT_EAST_4TH_AI | AI | DM6@bcd
DRIER_FLOW_STPT_EAST_CIP_AI | AI | DM8@bcd
DRIER_EAST_FLOW_STPT_SLOW | AI | DM900
DRIER_EAST_FLOW_STPT | AI | DM900
EAST_DRIER_FLOWRATE_STPT | AA | DM900 | EAST DRIER FLOWRATE SETPOINT
CHEM_DRIER_FLOWRATE_STPT | AI | DM900@bcd | DRIER FLOWRATE SETPOINT
DRIER_FROM_STER_CIP_STEP | AO | DM910
DRIER_BATCH_NUM_AR | AI | DM913 | (NGC) drier batch number ar
DRIER_BATCH_NUM_AI | AI | DM913 | drier batch number ar
DRIER_BATCH_NUM | AI | DM913 | Drier Batch Number
DRIER_BATCH_NUM_AO | AO | DM913 | drier batch number ao
DRIER_FLOW_AI | AI | DM920 | Gelatin Flow to Chemetator
CHEM_FLOW | AI | DM920 | CHEMETATOR FLOW
CHEM_FLOW_PASSTHRU | AI | DM920@BCD | CHEMETATOR FLOW
NEW_DRIER_FLOW | AA | DM920@BCD | DRIER FLOWRATE l/m
NEW_DRIER_FLOW_PASSTHRU | AA | DM920@BCD | DRIER FLOWRATE l/m
NEW_DRIER_FLOW_TO_DRY | AA | DM920@BCD | DRIER FLOWRATE l/m
DRIER_DRY_FLOW_EAST | AA | DM934 | COMIL FLOW
DRIER_DRY_FLOW_COMIL | AA | DM934 | COMIL DRY FLOW
DRIER_DRY_FLOW_FINE_GRIND_AA | AA | DM939 | FINE GRINDER FLOW VERY HIGH
DRIER_DRY_FLOW_FINE_GRIND | AA | DM939 | FINE GRINDER FLOW < 3.0
DRI_EAST_OSC_ARM_ON | DI | HR1.0
DRI_EAST_OSC_ARM_OFF | DI | HR1.0
DRIER_EAST_OSC_ARM_INVERT | DA | HR1.0
IDH_T51-3_PID_AUTO_MAN | DI | HR1.09 | T51-3 AUTO/MAN
T51-1_PID_LOOP_STATUS_DI | DI | HR1.2
T51-1_PID_LOOP_STATUS | DI | HR1.2 | (NGC)
T51-1_PID_LOOP_STATUS_DO | DO | HR1.2
T51-2_PID_LOOP_STATUS_DI | DI | HR1.3
T51-2_PID_LOOP_STATUS | DI | HR1.3 | (NGC)
T51-2_PID_LOOP_STATUS_DO | DO | HR1.3
T51-5_PID_LOOP_STATUS_DI | DI | HR1.4
T51-5_PID_LOOP_STATUS | DO | HR1.4
T51-3_S_PID_LOOP_STATUS_DI | DI | HR1.5
T51-3_S_PID_LOOP_STATUS | DI | HR1.5 | (NGC)
T51-3_S_PID_LOOP_STATUS_DO | DO | HR1.5
T51-12_PID_LOOP_STATUS_DI | DI | HR1.6
T51-12_PID_LOOP_STATUS | DI | HR1.6 | (NGC)
T51-12_PID_LOOP_STATUS_DO | DO | HR1.6
T51-3_W_PID_LOOP_STATUS_DI | DI | HR1.7
T51-3_W_PID_LOOP_STATUS | DI | HR1.7 | (NGC)
T51-3_W_PID_LOOP_STATUS_DO | DO | HR1.7
T51_12_SUMMER_WINTER | DI | HR1.8 | T51-12 Summer Winter Selection
DRIER_COOK_AI | AI | HR10
DRIER_COOK | AO | HR10
DRIER_FLOW_SPIKE_ALARM | DA | HR2.2 | DRIER FLOW SPIKE ALARM
DRIER_FLOW_SPIKE_ALARM_ACK_DO | DO | HR2.3
DRI_LOCAL_ALARM_DO | DO | HR3.0 | SIGNAL TO DRIER PLC TO TURN ON LOCAL ALM
DRI_LOCAL_ALM_LOCKOUT_DO | DO | HR3.1 | LOCKS OUT ALARM IN PLC
DRI_LOCAL_ALM_LOCKOUT_DI | DA | HR3.1 | LOCKS OUT ALARM IN PLC
DRIER_FLAG_EAST_1ST | DI | IR0.0
DRIER_FLAG_EAST_2ND | DI | IR0.2
DRIER_FLAG_EAST_3RD | DI | IR0.4
DRIER_FLAG_EAST_4TH | DI | IR0.6
DRIER_FLAG_EAST_CIP | DI | IR0.8
T51-1_PID_OUTPUT_FORCE | AO | IR101 | FORCE CC1 CONTROL VALVE (PID MAN ON)
T51-1_PID_OUTPUT | AA | IR101
T51-2_PID_OUTPUT_FORCE | AO | IR102 | FORCE CC2 CONTROL VALVE (PID MAN ON)
T51-2_PID_OUTPUT | AA | IR102
T51-5_PID_OUTPUT_FORCE | AO | IR103 | FORCE REGEN FAN (PID MAN ON)
T51-5_PID_OUTPUT | AA | IR103
T51-3_S_PID_OUTPUT_FORCE | AO | IR104 | FORCE CC3 CONTROL VALVE SUMM(PID MAN ON)
T51-3_S_PID_OUTPUT | AA | IR104
T51-12_OUTPUT_RAW | AI | IR105
T51-12_PID_OUTPUT_FORCE_TEST_R | AO | IR105 | FORCE GLYOL TEMP CONT VALVE (PID MAN ON)
T51-12_PID_OUTPUT_FORCE | AO | IR105 | FORCE GLYOL TEMP CONT VALVE (PID MAN ON)
T51-12_PID_OUTPUT | AA | IR105
T51-3_W_PID_OUTPUT_FORCE | AO | IR106 | FORCE CC1 CONTROL VALVE WINT(PID MAN ON)
T51-3_W_PID_OUTPUT | AA | IR106
FINE_GRIND_ALARM | DA | IR11.0 | FINE GRINDER IS STOPPED ALARM
DRIER_EAST_DOOR | DA | IR11.1 | East Drier Pin Breaker Stop
EAST_FLOW<11_L/M | DA | IR120.1 | N-Dryer 1st or 2nd flow < Target
CHEMETATOR_CIP_LOW_FLOW_ALARM | DI | IR120.13 | CHEMETATOR CIP LOW FLOW ALARM
EAST_FLOW<10_L/M | DA | IR120.3 | N-Dryer 3rd flow < Target
EAST_FLOW<8L/M | DA | IR120.5 | N-Dryer 4th flow < Target
T52-48_RAW | AA | IR182 | Small cooling tower outlet temp
T52-49_RAW | AA | IR183 | small cooling tower return from cc3
T52-50_RAW | AA | IR184 | cc3 inlet temp
RH51-1_RAW | AA | IR186 | relative humidity outside air
T51-5_RAW | AA | IR188 | IDH regen temp HI or LO
T51-4_SCADA_SCALED | AA | IR193 | Outside Air Temp
T51-10_ALARM | AA | IR195 | Chiller Outlet Temp Alarm Check Chiller
T51-10_SCADA_SCALED | AA | IR195 | Outlet Temperature from Carrier Chiller
T-51-10_RAW | AA | IR195 | chiller #1 outlet temp (cold)
T51-11_RAW | AA | IR196 | chiller #1 inlet temp (hot)
T51-11_SCADA_SCALED | AA | IR196 | Inlet to Carrier Chiller
T51-12_RAW | AA | IR197 | glycol temp after recirc pump
T51-12_RAW_SCADA_SCALING | AA | IR197 | glycol temp after recirc pump
SYS_WATCH_DRIER_CLOSE | DA | IR254.0 | MONITOR 1 MIN TIMER 254.0
SYS_WATCH_DRIER_OPEN | DA | IR254.0 | MONITOR 1 MIN TIMER 254.0
IDH_AV51-11_CLOSE | DO | IR38.0
IDH_AV51-11_OPEN | DO | IR38.1
IDH_AV51-12_CLOSE | DO | IR38.2
IDH_AV51-12_OPEN | DO | IR38.3
IDH_AV51-13_CLOSE | DO | IR38.4
IDH_AV51-13_OPEN | DO | IR38.5
IDH_12EF2_ZC_DO | DO | IR39.02 | IDH Economizer Zone2 valve Output
SWECO_VALVE_1 | DI | IR39.08 | N/C TO FINE GRINDER
SWECO_VALVE_2 | DI | IR39.09 | N/O TO 7 MESH
SWECO_VALVE_3 | DI | IR39.10 | N/O TO 7 MESH
SWECO_VALVE_4 | DI | IR39.11 | N/C TO FINE GRINDER
IDH_12EF2_ZH_DO | DO | IR42.08 | IDH Economizer Zone2 valve Opened
CHILLER1_COMP1 | DI | IR42.1
CHILLER#1_COMP#1 | DA | IR42.1 | chiller #1 comp #1
CHILLER#1_COMP#2 | DA | IR42.2 | chiller #1 comp #2
CHILLER#1_COMP#3 | DA | IR42.3 | chiller #1 comp #3
CHILLER#1_COMP#4 | DA | IR42.4 | chiller #1 comp #4
CHILLER#1_COMP#5 | DA | IR42.5 | chiller #1 comp #5
CHILLER#1_COMP#6 | DA | IR42.6 | chiller #1 comp #6
PU-51-1A_PROVE | DA | IR43.0 | chiller #1 recirc pump A
PU-51-2A_PROVE | DA | IR43.10 | chiller #2 recirc pump A
PU51-2B_PROVE | DA | IR43.12 | chiller #2 recirc pump B
PU52-2A_PROVE | DA | IR43.14 | small cooling tower recirc pump A
PU-51-1B_PROVE | DA | IR43.2 | chiller #1 recirc pump B
PU52-2B_PROVE | DA | IR44.0 | small cooling tower recirc pump B
INTAKE_BOTTOM_CLOSED | DI | IR44.08 | Intake bottom valve closed feedback
INTAKE_MIDDLE_CLOSED | DI | IR44.09 | Intake middle valve closed feedback
ZONE2_EXHAUST_FEEDBACK | DI | IR44.10 | Zone2 valve exhaust feedback
ZONE2_REC_FEEDBACK | DI | IR44.11 | Zone2 recirculation feedback
ZONE4_EXHAUST_FEEDBACK | DI | IR44.12 | Zone4 exhaust feedback
ZONE4_REC_FEEDBACK | DI | IR44.13 | Zone4 recirculation feedback
CHEM_PARK_POS_DRIER | DO | IR500.04 | Chemetator Park Position to Drier
DRIER_FLOW_PULSE_IN | DI | IR500.05 | Pulse from Flowmeter to SCADA
SWECO_7MESH_SELECTION | DI | IR500.06
SWECO_8MESH_SELECTION | DI | IR500.07
SWECO_20MESH_SELECTION | DI | IR500.08
SWECO_40MESH_SELECTION | DI | IR500.09
CHEM_OSCILLATING_DRIER | DO | IR500.14 | Chemetator Park Position to Drier
SWECO_7MESH_INDICATION | DI | IR501.00
SWECO_8MESH_INDICATION | DI | IR501.01
SWECO_20MESH_INDICATION | DI | IR501.02
SWECO_40MESH_INDICATION | DI | IR501.03 | SWECO 40/20M Indication
IDH_40M_MODIFIED | DI | IR501.05 | Modified 40M Selection
SWECO_40MESH_S_SELECTION | DI | IR501.05
SWECO_40MESH_S_INDICATION | DI | IR501.07 | SWECO 40/7M Indication
SWECO_8MESH_S_SELECTION | DI | IR501.08
SWECO_8MESH_S_INDICATION | DI | IR501.10
STERILIZER_OZONE_ALM | DI | IR501.11 | Sterilizer Ozone Leak Alarm
SWECO_WALTER_MESH_SELECTION | DI | IR501.12
SWECO_WALTER_MESH_INDICATION | DI | IR501.14
STERILIZER_OZONE_ALM2 | DI | IR501.15 | Sterilizer Ozone Trouble Alarm
CHILLER_NOT_RUNNING | DA | IR502.0 | Carrier Chiller Not Running
SWECO_REGRINDING_SELECTION | DI | IR502.03
SWECO_REGRINDING_INDICATION | DI | IR502.05
IDH_SATAKE_LSHH1 | DA | IR503.00 | Satake Level Switch 1 High High
IDH_SATAKE_LSH1 | DA | IR503.01 | Satake Level Switch 1 High
IDH_SATAKE_LSH2 | DA | IR503.02 | Satake Level Switch 2 High
IDH_SATAKE_FAULT | DA | IR503.03 | Satake Fault
IDH_SATAKE_SILENCE_PB | DI | IR503.04 | SATAKE Alarm Silence P.B.
IDH_SATAKE_CNTR_RESET_PB | DI | IR503.06 | SATAKE Counter Reset PB
IDH_SATAKE_STOP_BELT | DI | IR503.07 | SATAKE Command to Stop Comil
IDH_SATAKE_CNTR_STOP_PB | DI | IR503.08 | SATAKE Counter Stop and Reset P.B.
IDH_SATAKE_SILENCE | DI | IR503.10 | SATAKE Alarm Silence Status
IDH_SATAKE_CNTR_STOP | DI | IR503.11 | SATAKE Counter Status
IDH_SATAKE_BYPASS_MODE | DI | IR503.12 | SATAKE Bypass Mode - Prevent Comil Stopping on LSHH1

## PLC-SCADA_Compare
Original | Cleaned | PLC
DM2601 | DM2601 | 0.00
DM2603 | DM2603 | 0.01
DM2602 | DM2602 | 0.02
DM2604 | DM2604 | 0.03
DM100 | DM100 | 0.04
DM2653 | DM2653 | 0.05
DM2652 | DM2652 | 0.06
DM2651 | DM2651 | 0.07
DM2654 | DM2654 | 0.08
DM110 | DM110 | 0.09
DM130 | DM130 | 1.00
DM2753 | DM2753 | 1.01
DM2752 | DM2752 | 11.00
DM2751 | DM2751 | 11.01
DM2754 | DM2754 | 11.02
DM2853 | DM2853 | 11.04
DM2852 | DM2852 | 11.05
DM2851 | DM2851 | 11.06
DM2854 | DM2854 | 39.00
DM3501 | DM3501 | 39.01
DM3526 | DM3526 | 39.06
DM3516 | DM3516 | 39.07
DM3500 | DM3500 | 39.08
DM3521 | DM3521 | 39.09
DM3511 | DM3511 | 39.10
DM8@bcd | DM8@bcd | 39.11
DM6@bcd | DM6@bcd | 39.12
DM4@bcd | DM4@bcd | 39.13
DM2@bcd | DM2@bcd | 39.14
DM0@bcd | DM0@bcd | 39.15
DM920 | DM920 | 40.00
DM900 | DM900 | 42.01
DM2703 | DM2703 | 42.02
DM2702 | DM2702 | 42.03
DM2701 | DM2701 | 42.04
HR10 | HR10 | 42.05
DM913 | DM913 | 42.06
DM24@BCD | DM24@BCD | 44.01
DM27@BCD | DM27@BCD | 44.04
DM33@BCD | DM33@BCD | 44.05
DM30@BCD | DM30@BCD | 45.04
DM2704 | DM2704 | 45.05
DM223@BCD | DM223@BCD | 45.06
DM120 | DM120 | 45.07
DM222@BCD | DM222@BCD | 45.08
DM260 | DM260 | 50.00
DM221@BCD | DM221@BCD | 50.01
DM224 | DM224 | 50.02
DM2803 | DM2803 | 50.03
DM2802 | DM2802 | 50.06
IR105 | 105 | 50.07
DM2801 | DM2801 | 51.00
DM2804 | DM2804 | 60.00
DM140 | DM140 | 60.01
DM5211@BCD | DM5211@BCD | 60.02
DM5209@BCD | DM5209@BCD | 91.00
DM3499@BCD | DM3499@BCD | 91.01
DM900@bcd | DM900@bcd | 91.03
DM920@BCD | DM920@BCD | 92.00
DM10@BCD | DM10@BCD | 100
DM3501@BCD | DM3501@BCD | 101
HR1.0 | HR1.0 | 102
IR500.05 | 500.05 | 103
IR0.8 | 0.8 | 104
IR0.6 | 0.6 | 105
IR0.4 | 0.4 | 110
IR0.2 | 0.2 | 111
IR0.0 | 0.0 | 112
IR501.15 | 501.15 | 113
IR501.11 | 501.11 | 120.01
IR42.1 | 42.1 | 120.02
IR120.13 | 120.13 | 120.03
HR1.8 | HR1.8 | 120.04
HR1.6 | HR1.6 | 120.05
HR1.09 | HR1.09 | 120.06
IR501.05 | 501.05 | 120.07
HR1.4 | HR1.4 | 120.08
HR1.7 | HR1.7 | 120.09
HR1.5 | HR1.5 | 120.10
HR1.3 | HR1.3 | 120.11
HR1.2 | HR1.2 | 120.12
IR501.00 | 501.00 | 120.13
IR500.06 | 500.06 | 130
IR501.01 | 501.01 | 170
IR500.07 | 500.07 | 171
IR501.10 | 501.10 | 172
IR501.08 | 501.08 | 172.15
IR501.02 | 501.02 | 173
IR500.08 | 500.08 | 173.15
IR501.03 | 501.03 | 174
IR500.09 | 500.09 | 175
IR501.07 | 501.07 | 176
IR502.05 | 502.05 | 177
IR502.03 | 502.03 | 178
IR39.08 | 39.08 | 180
IR39.09 | 39.09 | 181
IR39.10 | 39.10 | 182
IR39.11 | 39.11 | 185
IR501.14 | 501.14 | 186
IR501.12 | 501.12 | 187
IR503.11 | 503.11 | 188
IR503.04 | 503.04 | 190
IR503.07 | 503.07 | 191
IR503.08 | 503.08 | 192
IR503.10 | 503.10 | 193
IR503.06 | 503.06 | 194
IR503.12 | 503.12 | 195
IR44.08 | 44.08 | 197
IR44.09 | 44.09 | 232.03
IR44.10 | 44.10 | 232.04
IR44.11 | 44.11 | 232.05
IR44.12 | 44.12 | 232.06
IR44.13 | 44.13 | 232.07
IR38.0 | 38.0 | 232.08
IR38.1 | 38.1 | 253.13
IR38.2 | 38.2 | 253.14
IR38.3 | 38.3 | 253.15
IR38.4 | 38.4 | 254.00
IR38.5 | 38.5 | 255.02
IR500.14 | 500.14 | 255.03
IR500.04 | 500.04 | 255.04
IR42.08 | 42.08 | 255.05
IR39.02 | 39.02 | 255.06
HR2.3 | HR2.3 | 255.07
HR3.0 | HR3.0 | 289.08
HR3.1 | HR3.1 | 300.00
DM5215@BCD | DM5215@BCD | 300.01
DM141 | DM141 | 300.02
IR103 | 103 | 300.03
DM910 | DM910 | 300.04
IR106 | 106 | 300.05
IR104 | 104 | 300.06
IR102 | 102 | 300.09
IR101 | 101 | 300.10
IR502.0 | 502.0 | 300.11
IR42.6 | 42.6 | b0830
IR42.5 | 42.5 | 500.00
IR42.4 | 42.4 | 500.01
IR42.3 | 42.3 | 500.02
IR42.2 | 42.2 | 500.03
IR11.1 | 11.1 | 500.04
HR2.2 | HR2.2 | 500.05
IR11.0 | 11.0 | 500.06
IR44.0 | 44.0 | 500.07
IR43.14 | 43.14 | 500.08
IR43.12 | 43.12 | 500.09
IR43.10 | 43.1 | 500.10
IR43.2 | 43.2 | 500.11
IR43.0 | 43.0 | 500.12
IR120.5 | 120.5 | 500.13
IR120.3 | 120.3 | 500.14
IR120.1 | 120.1 | 501.00
IR254.0 | 254.0 | 501.01
IR503.00 | 503.00 | 501.02
IR503.01 | 503.01 | 501.03
IR503.02 | 503.02 | 501.04
IR503.03 | 503.03 | 501.05
IR503.13 | 503.13 | 501.06
DM274 | DM274 | 501.07
IR193 | 193 | 501.08
DM314@BCD | DM314@BCD | 501.09
IR188 | 188 | 501.10
DM1767@BCD | DM1767@BCD | 501.11
DM1747@BCD | DM1747@BCD | 501.12
DM289@BCD | DM289@BCD | 501.13
DM255@BCD | DM255@BCD | 501.14
DM1790 | DM1790 | 501.15
IR195 | 195 | 502.00
IR196 | 196 | 502.01
DM1727 | DM1727 | 502.02
IR197 | 197 | 502.03
DM939 | DM939 | 502.04
DM934 | DM934 | 502.05
IR182 | 182 | 503.00
IR183 | 183 | 503.01
IR184 | 184 | 503.02
DM279@BCD | DM279@BCD | 503.03
IR186 | 186 | 503.04
DM1717 | DM1717 | 503.05
DM284@BCD | DM284@BCD | 503.06
DM210 | DM210 | 503.07
DM213 | DM213 | 503.08
DM1757 | DM1757 | 503.10
503.11
503.12
503.13
HR1.00
HR1.01
HR1.02
HR1.03
HR1.04
HR1.05
HR1.06
HR1.07
HR1.08
HR1.09
HR1.10
HR1.11
HR2.00
HR2.01
HR2.02
HR2.03
HR2.04
HR2.05
HR2.06
HR2.07
HR2.08
HR2.09
HR2.10
HR2.11
HR2.12
HR3.00
HR3.01
HR10.00
HR10.01
HR10.02
HR10.03
AR01.00
AR01.01
AR01.02
AR01.03
AR01.07
AR01.08
AR01.09
TIM000(bit)
TIM005(bit)
TIM006(bit)
TIM010(bit)
TIM015(bit)
TIM016(bit)
TIM017(bit)
TIM021(bit)
TIM022(bit)
TIM023(bit)
TIM024(bit)
TIM025(bit)
TIM026(bit)
TIM027(bit)
TIM028(bit)
TIM029(bit)
TIM032(bit)
TIM033(bit)
TIM034(bit)
TIM035(bit)
TIM036(bit)
TIM037(bit)
TIM038(bit)
TIM039(bit)
TIM060(bit)
TIM062(bit)
TIM063(bit)
TIM064(bit)
TIM065(bit)
TIM066(bit)
TIM068(bit)
TIM069(bit)
CNT020
CNT030
CNT031(bit)
CNT041(bit)
CNT051(bit)
CNT052(bit)
CNT061
CNT061(bit)
DM0
DM1
DM2
DM3
DM4
DM5
DM6
DM7
DM8
DM9
DM10
DM24
DM25
DM27
DM28
DM30
DM31
DM33
DM34
DM100
DM102
DM104
DM106
DM110
DM112
DM114
DM116
DM120
DM122
DM124
DM126
DM130
DM132
DM134
DM136
DM140
DM141
DM142
DM144
DM147
DM148
DM149
DM150
DM180
DM184
DM200
DM204
DM215
DM217
DM220
DM221
DM222
DM223
DM224
DM225
DM226
DM255
DM256
DM257
DM258
DM259
DM260
DM261
DM270
DM274
DM275
DM279
DM280
DM284
DM285
DM289
DM300
DM304
DM310
DM314
DM500
DM501
DM502
DM503
DM505
DM506
DM508
DM509
DM510
DM511
DM512
DM513
DM515
DM800
DM801
DM900
DM901
DM902
DM910
DM920
DM930
DM934
DM935
DM939
DM1121
DM1122
DM1123
DM1170
DM1171
DM1712
DM1717
DM1720
DM1721
DM1722
DM1727
DM1728
DM1730
DM1731
DM1732
DM1737
DM1738
DM1740
DM1741
DM1742
DM1747
DM1750
DM1751
DM1752
DM1757
DM1760
DM1761
DM1762
DM1767
DM1770
DM1771
DM1772
DM1777
DM1780
DM1781
DM1782
DM1787
DM1790
DM1821
DM1886
DM1921
DM2600
DM2650
DM2700
DM2750
DM2800
DM2801
DM2802
DM2803
DM2804
DM2805
DM2806
DM2850
DM3000
DM3001
DM3002
DM3005
DM3006
DM3007
DM3008
DM3009
DM3143
DM3148
DM3499
DM3500
DM3501
DM3505
DM3506
DM3521
DM3526
DM3553
DM3558
DM3563
DM3568
DM3573
DM3578
DM3603
DM3608
DM3613
DM3618
DM3623
DM3628
DM3800
DM3801
DM3802
DM3803
DM3804
DM3805
DM3806
DM3807
DM3808
DM3809
DM3810
DM3811
DM4000
DM4005
DM5200
DM5201
DM5202
DM5203
DM5204
DM5205
DM5209
DM5210
DM5211
DM5212
DM5213
DM5215
DM5217
DM5221
DM5209
DM5210
DM5211
DM5212
DM5213
DM5215
DM5217
DM5221

## SCADA_IO
Name | Type | Unit Type | Units | Other Descriptors | Screen | To be Verified? | SCADA Tags Used | Corresponding PLC Tag | Notes
12EF2 | Visual | N/A | N/A | Exhaust | IDH Mimic |  | From Drier PLC | From Drier PLC
12EF4 | Visual | N/A | N/A | Exhaust | IDH Mimic |  | From Drier PLC | From Drier PLC
12EF2-Exhaust Block | Visual | N/A | N/A | Exhaust (Top Left) | IDH Mimic |  | ZONE2_EXHAUST_FEEDBACK | OMR_GW2.IDH.IR44.10
12EF2-Recirc Block | Visual | N/A | N/A | Exhaust (Top Left) | IDH Mimic |  | ZONE2_REC_FEEDBACK | OMR_GW2.IDH.IR44.11
12EF2-Recirc Button | Button | N/A | N/A | Exhaust (Top Left) | IDH Mimic |  | ZONE2_REC_COMMAND | OMR_GW2.IDH.IR39.02
12EF4-Exhaust Block | Visual | N/A | N/A | Exhaust (Top Left) | IDH Mimic |  | ZONE4_EXHAUST_FEEDBACK | OMR_GW2.IDH.IR44.12
12EF4-Recirc Block | Visual | N/A | N/A | Exhaust (Top Left) | IDH Mimic |  | ZONE4_REC_FEEDBACK | OMR_GW2.IDH.IR44.13
12EF4-Recirc Button | Button | N/A | N/A | Exhaust (Top Left) | IDH Mimic |  | ZONE4_REC_COMMAND | OMR_GW2.IDH.IR39.03
Regen Fan | AI | Current | Amps | Air Out (Top Left) | IDH Mimic |  | IDH_REGEN_FAN_AMPS | OMR_GW2.IDH.DM1747@BCD
Exhaust | AI | Temperature | C | Air Out (Top Left) | IDH Mimic |  | T51-5 (Calc. from T51-5_Raw) | OMR_GW2.IDH.IR188
Air Temp (air in) | AI | Temperature | C | Air In (Top right) | IDH Mimic |  | RGN_BNR_01_AIR_TEMP | From ABR_CLPX PLC
Air Temp SP | AI | Temperature | C | Air In (Top right) | IDH Mimic |  | IDH_REGEN_BURNER_SP | From ABR_CLPX PLC
RGN_BNR | AI | % | % | Air In (Top right) | IDH Mimic |  | RGN_BNR_01_VLV_CV | From ABR_CLPX PLC
Gas Meter | AI | Air Flow | m3/h | Air In (Top right) | IDH Mimic |  | IDH_BURNER_GAS Opens Trend TRD.grf w/ IDH Total.csv | From ABR_CLPX PLC
Gas Meter Trend |  |  |  |  | Trend Popup |  | See trend list | See trend list
Batch Number | INT | N/A | N/A | N/A | IDH Mimic |  | DRIER_BATCH_NUM | OMR_GW2.IDH.DM913
T51-4 | AI | Temperature | C | Air In (Center Left) | IDH Mimic |  | T51-4 (Calc. from T51-4_SCADA_SCALED) | OMR_GW2.IDH.IR193
RH51-1 | AI | % | % | Air In (Center Left) | IDH Mimic |  | RH51-1 (Calc. from RH51-1_Raw) | OMR_GW2.IDH.IR186
Delta | AI | Temperature | C | Center | IDH Mimic |  | T51-4_T51-1_DELTA (calc. 51-4 - 51-1) | calculated tag
T51-1 | AI | Temperature | C | Center | IDH Mimic |  | T51-1 (calc. from T51-1_SCADA_SCALED) | OMR_GW2.IDH.DM284@BCD
T51-2 | AI | Temperature | C | Center | IDH Mimic |  | T51-2 (calc. from T51-2_SCADA_SCALED) | OMR_GW2.IDH.DM279@BCD
T51-6 | AI | Temperature | C | Center | IDH Mimic |  | T51-6 (calc. from T51-6_SCADA_SCALED) | OMR_GW2.IDH.DM289@BCD
Main Fan | AI | Current | Amps | Center | IDH Mimic |  | IDH_MAIN_FAN_AMPS | OMR_GW2.IDH.DM1767@BCD
T51-3 | AI | Temperature | C | Air Out (Center Right) | IDH Mimic |  | T51-3 (Calc. from T51-3_Raw) | OMR_GW2.IDH.DM274
Air Temp (air out) | AI | Temperature | C | Air Out (Center Right) | IDH Mimic |  | DRY_D_12TT1_I (calc from DRY_D_12TT1_AA) | from OMR_FINS PLC
Dew Point | AI | Temperature | C | Air Out (Center Right) | IDH Mimic |  | DRY_DEWPOINT_AI | from OMR_FINS PLC
T51-10 | AI | Temperature | C | Chiller (Bottom Left) | IDH Mimic |  | T51-10_SCADA_SCALED_CA (calc from T51-10_SCADA_SCALED) | OMR_GW2.IDH.IR195
T51-11 | AI | Temperature | C | Chiller (Bottom Left) | IDH Mimic |  | T51-11_SCADA_SCALED_CA (calc from T51-11_SCADA_SCALED) | OMR_GW2.IDH.IR196
T51-12 | AI | Temperature | C | Chiller (Bottom Left) | IDH Mimic |  | EVAP_IDH_TT51_12_PV | From ABR_EVAP PLC
TCV51-3 | Valve | N/A | N/A | Chiller (Bottom Left) | IDH Mimic |  | EVAP_IDH_TIC51_3_CV (Open %, from PID) | From ABR_EVAP PLC
PU-51-1A | Pump | N/A | N/A | Chiller (Bottom Left) | IDH Mimic |  | PU51-1A_PROVE | OMR_GW2.IDH.IR43.0
PU-51-1B | Pump | N/A | N/A | Chiller (Bottom Left) | IDH Mimic |  | PU51-1B_PROVE | OMR_GW2.IDH.IR43.2
New CO #1-6 | Visual | ? | N/A | Chiller (Bottom Left) | IDH Mimic | X | n/a | n/a | These are compressors - currently not connected
Large Cooling Tower | AI | Temperature | C | Bottom | IDH Mimic |  | TR706 | From ABR_EVAP PLC
T-52-48 | AI | Temperature | C | Small Cooling Tower | IDH Mimic |  | T52-48 (from _Raw tag) | OMR_GW2.IDH.IR182
T-52-49 | AI | Temperature | C | Small Cooling Tower | IDH Mimic |  | T52-49 (from _Raw tag) | OMR_GW2.IDH.IR183
T-52-50 | AI | Temperature | C | Small Cooling Tower | IDH Mimic |  | T52-50 (from _Raw tag) | OMR_GW2.IDH.IR184
TCV51-8 | Valve | N/A | N/A | Small Cooling Tower | IDH Mimic | X | Open%: EVAP_IDH_TIC51_8_CV FB Colour: EVAP_IDH_TIC51_8_CV | From ABR_EVAP PLC | Same name?
TCV51-8 | Valve | N/A | N/A | Small Cooling Tower | IDH Mimic | X | Open%: 100 - EVAP_IDH_TIC51_8_CV FB Colour: 100 - EVAP_IDH_TIC51_8_CV | From ABR_EVAP PLC | Same name?
PU-52-2A | Pump | N/A | N/A | Small Cooling Tower | IDH Mimic |  | PU52-2A_PROVE | OMR_GW2.IDH.IR43.14
PU-52-2B | Pump | N/A | N/A | Small Cooling Tower | IDH Mimic |  | PU52-2B_PROVE | OMR_GW2.IDH.IR44.0
CC1 T51-1 Mode | DI | N/A | N/A |  | IDH PID
CC1 T51-1 PV | Float | % | N/A |  | IDH PID
CC1 T51-1 SP | Float | % | N/A |  | IDH PID
CC1 T51-1 OUT | INT | % | N/A |  | IDH PID
CC1 T51-1 Force | INT | N/A | N/A |  | IDH PID
CC1 T51-1 Kp | INT | N/A | N/A |  | IDH PID
CC1 T51-1 Ki | INT | N/A | N/A |  | IDH PID
CC1 T51-1 Kd | INT | N/A | N/A |  | IDH PID
CC1 T51-1 Sample | INT | N/A | N/A |  | IDH PID
CC2 T51-2 Mode | DI | N/A | N/A |  | IDH PID
CC2 T51-2 PV | Float | % | N/A |  | IDH PID
CC2 T51-2 SP | Float | % | N/A |  | IDH PID
CC2 T51-2 OUT | INT | % | N/A |  | IDH PID
CC2 T51-2 Force | INT | N/A | N/A |  | IDH PID
CC2 T51-2 Kp | INT | N/A | N/A |  | IDH PID
CC2 T51-2 Ki | INT | N/A | N/A |  | IDH PID
CC2 T51-2 Kd | INT | N/A | N/A |  | IDH PID
CC2 T51-2 Sample | INT | N/A | N/A |  | IDH PID
Regen T51-5 Mode | DI | N/A | N/A |  | IDH PID
Regen T51-5 PV | Float | % | N/A |  | IDH PID
Regen T51-5 SP | Float | % | N/A |  | IDH PID
Regen T51-5 OUT | INT | % | N/A |  | IDH PID
Regen T51-5 Force | INT | N/A | N/A |  | IDH PID
Regen T51-5 Kp | INT | N/A | N/A |  | IDH PID
Regen T51-5 Ki | INT | N/A | N/A |  | IDH PID
Regen T51-5 Kd | INT | N/A | N/A |  | IDH PID
Regen T51-5 Sample | INT | N/A | N/A |  | IDH PID
PU-51-1A | Pump | N/A |  |  | IDH Season
PU-51-1B | Pump | N/A |  |  | IDH Season
AV51-0010 | Analog Valve | % |  |  | IDH Season
AV51-2 | Analog Valve | % |  |  | IDH Season
AV51-11 | Valve | N/A |  |  | IDH Season
AV51-12 | Valve | N/A |  |  | IDH Season
AV51-13 | Valve | N/A |  |  | IDH Season
T51-10 | AI | Temperature | C |  | IDH Season
T51-11 | AI | Temperature | C |  | IDH Season
T51-12 | AI | Temperature | C |  | IDH Season
T51-12 SP | AI | Temperature | C |  | IDH Season
INLET TEMP HIGH LIMIT |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
INLET TEMP LOW LIMIT |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
INLET HUMIDITY HIGH LIMIT |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
INLET HUMIDITY LOW LIMIT |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
HOT WATER SUPPLY LOW LIMIT |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
HOT WATER BYPASS DELAY |  | Time | s |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
HOT WATER SUPPLY SP |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
HOT WATER TEMP RELEASE SP |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
MINIMUM NUMBER OF FANS FOR TEMP CONTROL RELEASE |  | N/A | N/A |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
UPPER LEVEL MAX TEMP LIMIT VALVE CLOSED |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
LOWER LEVEL MAX TEMP LIMIT VALVE CLOSED |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
INLET TEMP BOUND EXCEEDING DELAY |  | Time | s |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
HOT WATER TEMP BOUND EXCEEDING DELAY |  | Time | s |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BELT SPEED CHEMETATOR ON |  | ? | m/h |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BELT SPEED CHEMETATOR OFF |  | ? | m/h |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
MANUAL SMALL VALVE HOT WATER SUPPLY |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BIG VALVE RELEASE |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BIG VALVE BLOCKING |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BIG VALVE DEAD ZONE |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BIG VALVE SHUT DOWN DELAY |  | Time | s |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
MANUAL BIG VALVE HOT WATER SUPPLY |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BELT SPEED SP |  | ? | m/h |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
BELT SPEED UPPER LIMIT |  | ? | m/h |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
LEADING PUMP DAY |  | ? | ? |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
LEADING PUMP TIME |  | ? | ? |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
MANUAL SP FREQUENCY CONTROLLER |  | % | % |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
INLET HUMIDITY BOUND EXCEEDING DELAY |  | Time | s |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
PUMPS AFTER RUN |  | Time | s |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
TIME DELAY BREAKER RUNNING OFF |  | Time | s |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
SETPOINT RELEASE TUNNEL VENTILATION |  | Temperature | C |  | 0 / SP Screen | x |  | All include "SET" and "REAL"
Note on H2: Microsoft Office User: Need to check if this is indeed dynamic and linked to the PLC

## All_SCADA_Tags
Type | TAG | NEXT BLK | DESCRIPTION | Full Address | Clean_Address_BCD | Clean_Address
DA | IDH_SATAKE_BYPASS_REMINDER |  | SATAKE Bypass Enabled with No Alarms Present | OMR_GW2.IDH. IR503.13 | IR503.13 | IR503.13
AI | DRIER_FLOW_STPT_EAST_1ST_AI |  |  | OMR_GW2.IDH.DM0@bcd | DM0@bcd | DM0
AI | IDH_SATAKE_COUNTER_PV |  | SATAKE Counter Value | OMR_GW2.IDH.DM10@BCD | DM10@BCD | DM10
AA | T51-1_STPT |  |  | OMR_GW2.IDH.DM100 | DM100 | DM100
AA | T51-2_STPT |  |  | OMR_GW2.IDH.DM110 | DM110 | DM110
AA | T51-5_STPT |  |  | OMR_GW2.IDH.DM120 | DM120 | DM120
AA | T51-3_STPT |  |  | OMR_GW2.IDH.DM130 | DM130 | DM130
AO | T51-12_STPT_AO |  |  | OMR_GW2.IDH.DM140 | DM140 | DM140
AO | T51-12_MAN_OUTPUT |  | T51-12 MANUAL OUTPUT (AV51-2) | OMR_GW2.IDH.DM141 | DM141 | DM141
AA | CFM_51-1 | CFM_51-1_TREND | IDH AIR FLOW | OMR_GW2.IDH.DM1717 | DM1717 | DM1717
AA | EAST_DRIER_FLOW | EAST_DRIER_FLOW_TOTAL | EAST DRIER FLOWRATE | OMR_GW2.IDH.DM1727 | DM1727 | DM1727
AA | IDH_REGEN_FAN_AMPS |  | IDH REGEN FAN AMPS | OMR_GW2.IDH.DM1747@BCD | DM1747@BCD | DM1747
AA | DEW_51-1_RAW | DEW_51-1 |  | OMR_GW2.IDH.DM1757 | DM1757 | DM1757
AA | IDH_MAIN_FAN_AMPS |  | IDH main fan amps | OMR_GW2.IDH.DM1767@BCD | DM1767@BCD | DM1767
AA | L52-51 | L52-51_TREND | Chiller Tank lvl high or low | OMR_GW2.IDH.DM1790 | DM1790 | DM1790
AI | DRIER_FLOW_STPT_EAST_2ND_AI |  |  | OMR_GW2.IDH.DM2@bcd | DM2@bcd | DM2
AA | CHEM_TEST_FLOW_AVG_1 |  | CHEMETATOR FLOW AVG (minute) | OMR_GW2.IDH.DM210 | DM210 | DM210
AA | CHEM_TEST_FLOW_AVG_2 |  | CHEMETATOR FLOW AVG (hour) | OMR_GW2.IDH.DM213 | DM213 | DM213
AI | IDH_T51-3_PROPORTIONAL |  | T51-3 PROPORTIONAL | OMR_GW2.IDH.DM221@BCD | DM221@BCD | DM221
AI | IDH_T51-3_INTEGRAL |  | T51-3 INTEGRAL | OMR_GW2.IDH.DM222@BCD | DM222@BCD | DM222
AI | IDH_T51-3_DERIVATIVE |  | T51-3 DERIVATIVE | OMR_GW2.IDH.DM223@BCD | DM223@BCD | DM223
AI | IDH_T51-3_SAMPLE |  | T51-3 SAMPLE PERIOD | OMR_GW2.IDH.DM224 | DM224 | DM224
AI | IDH_40M_VALVE_TIME_OFF |  | V2 Closed Time (minutes) | OMR_GW2.IDH.DM24@BCD | DM24@BCD | DM24
AA | IDH_T51-3_SETPOINT |  | T51-3 SETPOINT | OMR_GW2.IDH.DM255@BCD | DM255@BCD | DM255
AI | IDH_T51-3_OUTPUT |  | T51-3 OUTPUT | OMR_GW2.IDH.DM260 | DM260 | DM260
AI | T-51-1_PROPORTIONAL |  | (NGC) | OMR_GW2.IDH.DM2601 | DM2601 | DM2601
AI | T51-1_INTEGRAL |  | (NGC) | OMR_GW2.IDH.DM2602 | DM2602 | DM2602
AI | T51-1_DERIVATIVE |  | (NGC) | OMR_GW2.IDH.DM2603 | DM2603 | DM2603
AI | T51-1_SAMPLING |  | (NGC) | OMR_GW2.IDH.DM2604 | DM2604 | DM2604
AI | T51-2_PROPORTIONAL |  | (NGC) | OMR_GW2.IDH.DM2651 | DM2651 | DM2651
AI | T51-2_INTEGRAL |  | (NGC) | OMR_GW2.IDH.DM2652 | DM2652 | DM2652
AI | T51-2_DERIVATIVE |  | (NGC) | OMR_GW2.IDH.DM2653 | DM2653 | DM2653
AI | T51-2_SAMPLING |  | (NGC) | OMR_GW2.IDH.DM2654 | DM2654 | DM2654
AI | IDH_40M_VALVE_TIME_ON |  | V2 Open Time (seconds) | OMR_GW2.IDH.DM27@BCD | DM27@BCD | DM27
AI | T51-5_PROPORTIONAL |  | (NGC) | OMR_GW2.IDH.DM2701 | DM2701 | DM2701
AI | T51-5_INTEGRAL |  | (NGC) | OMR_GW2.IDH.DM2702 | DM2702 | DM2702
AI | T51-5_DERIVATIVE |  | (NGC) | OMR_GW2.IDH.DM2703 | DM2703 | DM2703
AI | T51-5_SAMPLING |  | (NGC) | OMR_GW2.IDH.DM2704 | DM2704 | DM2704
AA | T51-3_RAW | T51-3 | DRIER TEMP IN FROM IDH | OMR_GW2.IDH.DM274 | DM274 | DM274
AI | T51-3_S_PROPORTIONAL |  | (NGC) | OMR_GW2.IDH.DM2751 | DM2751 | DM2751
AI | T51-3_S_INTEGRAL |  | (NGC) | OMR_GW2.IDH.DM2752 | DM2752 | DM2752
AI | T51-3_S_DERIVATIVE |  | (NGC) | OMR_GW2.IDH.DM2753 | DM2753 | DM2753
AI | T51-3_S_SAMPLING |  | (NGC) | OMR_GW2.IDH.DM2754 | DM2754 | DM2754
AA | T51-2_SCADA_SCALED | T51-2 | Air Temp Before Dessicant Wheel | OMR_GW2.IDH.DM279@BCD | DM279@BCD | DM279
AI | T51-12_PROPORTIONAL |  | (NGC) | OMR_GW2.IDH.DM2801 | DM2801 | DM2801
AI | T51-12_INTEGRAL |  | (NGC) | OMR_GW2.IDH.DM2802 | DM2802 | DM2802
AI | T51-12_DERIVATIVE |  | (NGC) | OMR_GW2.IDH.DM2803 | DM2803 | DM2803
AI | T51-12_SAMPLING |  | (NGC) | OMR_GW2.IDH.DM2804 | DM2804 | DM2804
AA | T51-1_SCADA_SCALED | T51-1 | Air Temp After CC1 | OMR_GW2.IDH.DM284@BCD | DM284@BCD | DM284
AI | T51-3_W_PROPORTIONAL |  | (NGC) | OMR_GW2.IDH.DM2851 | DM2851 | DM2851
AI | T51-3_W_INTEGRAL |  | (NGC) | OMR_GW2.IDH.DM2852 | DM2852 | DM2852
AI | T51-3_W_DERIVATIVE |  | (NGC) | OMR_GW2.IDH.DM2853 | DM2853 | DM2853
AI | T51-3_W_SAMPLING |  | (NGC) | OMR_GW2.IDH.DM2854 | DM2854 | DM2854
AA | T51-6_SCADA_SCALED | T51-6 | After Wheel Temp | OMR_GW2.IDH.DM289@BCD | DM289@BCD | DM289
AI | IDH_40_7M_VALVE_TIME_ON |  | V3 Open Time (seconds) | OMR_GW2.IDH.DM30@BCD | DM30@BCD | DM30
AA | T51-5_PV_TO_BURNER_AA | T51-5_PV_TO_BURNER_CA | IDH regen temp HI or LO | OMR_GW2.IDH.DM314@BCD | DM314@BCD | DM314
AI | IDH_40_7M_VALVE_TIME_OFF |  | V3 Closed Time (seconds) | OMR_GW2.IDH.DM33@BCD | DM33@BCD | DM33
AI | STER_P66_SETPOINT |  | P66 Speed Setpoint | OMR_GW2.IDH.DM3499@BCD | DM3499@BCD | DM3499
AO | DRI_CONT_P116_SP_AO |  | p116 controller stpt ao | OMR_GW2.IDH.DM3500 | DM3500 | DM3500
AI | STER_P117_SETPOINT |  | P117 Speed Setpoint | OMR_GW2.IDH.DM3501@BCD | DM3501@BCD | DM3501
AI | DRI_CONT_P116_PV |  | P116 CONTROLLER PV | OMR_GW2.IDH.DM3511 | DM3511 | DM3511
AI | DRI_CONT_P118_PV |  | P118 CONTROLLER PV | OMR_GW2.IDH.DM3516 | DM3516 | DM3516
AI | DRI_CONT_P116_SP_AI |  | p116 controller stpt ai | OMR_GW2.IDH.DM3521 | DM3521 | DM3521
AI | DRI_CONT_P118_SP_AI |  | P118 CONTROLLER PV | OMR_GW2.IDH.DM3526 | DM3526 | DM3526
AI | DRIER_FLOW_STPT_EAST_3RD_AI |  |  | OMR_GW2.IDH.DM4@bcd | DM4@bcd | DM4
AI | CC3_TEMPERATURE | CC3_TEMPERATURE_CA | IDH Outlet Temperature | OMR_GW2.IDH.DM5209@BCD | DM5209@BCD | DM5209
AI | CC3_OUTPUT |  | CC3 Cooling Valve Output | OMR_GW2.IDH.DM5211@BCD | DM5211@BCD | DM5211
AO | CC3_SETPOINT_AO |  | CC3 Setpoint Out | OMR_GW2.IDH.DM5215@BCD | DM5215@BCD | DM5215
AI | DRIER_FLOW_STPT_EAST_4TH_AI |  |  | OMR_GW2.IDH.DM6@bcd | DM6@bcd | DM6
AI | DRIER_FLOW_STPT_EAST_CIP_AI |  |  | OMR_GW2.IDH.DM8@bcd | DM8@bcd | DM8
AI | DRIER_EAST_FLOW_STPT | DRIER_EAST_FLOW_STPT_TOTAL |  | OMR_GW2.IDH.DM900 | DM900 | DM900
AO | DRIER_FROM_STER_CIP_STEP |  |  | OMR_GW2.IDH.DM910 | DM910 | DM910
AI | DRIER_BATCH_NUM |  | Drier Batch Number | OMR_GW2.IDH.DM913 | DM913 | DM913
AI | CHEM_FLOW | CHEM_FLOW_AVG | CHEMETATOR FLOW | OMR_GW2.IDH.DM920 | DM920 | DM920
AA | DRIER_DRY_FLOW_EAST | DRIER_DRY_FLOW_EAST_TOTAL | COMIL FLOW | OMR_GW2.IDH.DM934 | DM934 | DM934
AA | DRIER_DRY_FLOW_FINE_GRIND | DRIER_DRY_FLOW_FINE_TOTAL | FINE GRINDER FLOW < 3.0 | OMR_GW2.IDH.DM939 | DM939 | DM939
DI | DRI_EAST_OSC_ARM_ON | DRI_EAST_OSC_ARM_ON_TIMESTAMP |  | OMR_GW2.IDH.HR1.0 | HR1.0 | HR1.0
DI | IDH_T51-3_PID_AUTO_MAN |  | T51-3 AUTO/MAN | OMR_GW2.IDH.HR1.09 | HR1.09 | HR1.09
DI | T51-1_PID_LOOP_STATUS |  | (NGC) | OMR_GW2.IDH.HR1.2 | HR1.2 | HR1.2
DI | T51-2_PID_LOOP_STATUS |  | (NGC) | OMR_GW2.IDH.HR1.3 | HR1.3 | HR1.3
DO | T51-5_PID_LOOP_STATUS |  |  | OMR_GW2.IDH.HR1.4 | HR1.4 | HR1.4
DI | T51-3_S_PID_LOOP_STATUS |  | (NGC) | OMR_GW2.IDH.HR1.5 | HR1.5 | HR1.5
DI | T51-12_PID_LOOP_STATUS |  | (NGC) | OMR_GW2.IDH.HR1.6 | HR1.6 | HR1.6
DI | T51-3_W_PID_LOOP_STATUS |  | (NGC) | OMR_GW2.IDH.HR1.7 | HR1.7 | HR1.7
DI | T51_12_SUMMER_WINTER |  | T51-12 Summer Winter Selection | OMR_GW2.IDH.HR1.8 | HR1.8 | HR1.8
AO | DRIER_COOK |  |  | OMR_GW2.IDH.HR10 | HR10 | HR10
DA | DRIER_FLOW_SPIKE_ALARM |  | DRIER FLOW SPIKE ALARM | OMR_GW2.IDH.HR2.2 | HR2.2 | HR2.2
DO | DRIER_FLOW_SPIKE_ALARM_ACK_DO |  |  | OMR_GW2.IDH.HR2.3 | HR2.3 | HR2.3
DO | DRI_LOCAL_ALARM_DO |  | SIGNAL TO DRIER PLC TO TURN ON LOCAL ALM | OMR_GW2.IDH.HR3.0 | HR3.0 | HR3.0
DO | DRI_LOCAL_ALM_LOCKOUT_DO |  | LOCKS OUT ALARM IN PLC | OMR_GW2.IDH.HR3.1 | HR3.1 | HR3.1
DI | DRIER_FLAG_EAST_1ST |  |  | OMR_GW2.IDH.IR0.0 | IR0.0 | IR0.0
DI | DRIER_FLAG_EAST_2ND |  |  | OMR_GW2.IDH.IR0.2 | IR0.2 | IR0.2
DI | DRIER_FLAG_EAST_3RD |  |  | OMR_GW2.IDH.IR0.4 | IR0.4 | IR0.4
DI | DRIER_FLAG_EAST_4TH |  |  | OMR_GW2.IDH.IR0.6 | IR0.6 | IR0.6
DI | DRIER_FLAG_EAST_CIP |  |  | OMR_GW2.IDH.IR0.8 | IR0.8 | IR0.8
AO | T51-1_PID_OUTPUT_FORCE |  | FORCE CC1 CONTROL VALVE (PID MAN ON) | OMR_GW2.IDH.IR101 | IR101 | IR101
AO | T51-2_PID_OUTPUT_FORCE |  | FORCE CC2 CONTROL VALVE (PID MAN ON) | OMR_GW2.IDH.IR102 | IR102 | IR102
AO | T51-5_PID_OUTPUT_FORCE |  | FORCE REGEN FAN (PID MAN ON) | OMR_GW2.IDH.IR103 | IR103 | IR103
AO | T51-3_S_PID_OUTPUT_FORCE |  | FORCE CC3 CONTROL VALVE SUMM(PID MAN ON) | OMR_GW2.IDH.IR104 | IR104 | IR104
AO | T51-12_PID_OUTPUT_FORCE |  | FORCE GLYOL TEMP CONT VALVE (PID MAN ON) | OMR_GW2.IDH.IR105 | IR105 | IR105
AO | T51-3_W_PID_OUTPUT_FORCE |  | FORCE CC1 CONTROL VALVE WINT(PID MAN ON) | OMR_GW2.IDH.IR106 | IR106 | IR106
DA | FINE_GRIND_ALARM |  | FINE GRINDER IS STOPPED ALARM | OMR_GW2.IDH.IR11.0 | IR11.0 | IR11.0
DA | DRIER_EAST_DOOR |  | East Drier Pin Breaker Stop | OMR_GW2.IDH.IR11.1 | IR11.1 | IR11.1
DA | EAST_FLOW<11_L/M |  | N-Dryer 1st or 2nd flow < Target | OMR_GW2.IDH.IR120.1 | IR120.1 | IR120.1
DI | CHEMETATOR_CIP_LOW_FLOW_ALARM |  | CHEMETATOR CIP LOW FLOW ALARM | OMR_GW2.IDH.IR120.13 | IR120.13 | IR120.13
DA | EAST_FLOW<10_L/M |  | N-Dryer 3rd flow < Target | OMR_GW2.IDH.IR120.3 | IR120.3 | IR120.3
DA | EAST_FLOW<8L/M |  | N-Dryer 4th flow < Target | OMR_GW2.IDH.IR120.5 | IR120.5 | IR120.5
AA | T52-48_RAW | T52-48 | Small cooling tower outlet temp | OMR_GW2.IDH.IR182 | IR182 | IR182
AA | T52-49_RAW | T52-49 | small cooling tower return from cc3 | OMR_GW2.IDH.IR183 | IR183 | IR183
AA | T52-50_RAW | T52-50 | cc3 inlet temp | OMR_GW2.IDH.IR184 | IR184 | IR184
AA | RH51-1_RAW | RH51-1 | relative humidity outside air | OMR_GW2.IDH.IR186 | IR186 | IR186
AA | T51-5_RAW | T51-5 | IDH regen temp HI or LO | OMR_GW2.IDH.IR188 | IR188 | IR188
AA | T51-4_SCADA_SCALED | T51-4 | Outside Air Temp | OMR_GW2.IDH.IR193 | IR193 | IR193
AA | T-51-10_RAW | T51-10 | chiller #1 outlet temp (cold) | OMR_GW2.IDH.IR195 | IR195 | IR195
AA | T51-11_RAW | T51-11 | chiller #1 inlet temp (hot) | OMR_GW2.IDH.IR196 | IR196 | IR196
AA | T51-12_RAW | T51-12 | glycol temp after recirc pump | OMR_GW2.IDH.IR197 | IR197 | IR197
DA | SYS_WATCH_DRIER_CLOSE |  | MONITOR 1 MIN TIMER 254.0 | OMR_GW2.IDH.IR254.0 | IR254.0 | IR254.0
DO | IDH_AV51-11_CLOSE |  |  | OMR_GW2.IDH.IR38.0 | IR38.0 | IR38.0
DO | IDH_AV51-11_OPEN |  |  | OMR_GW2.IDH.IR38.1 | IR38.1 | IR38.1
DO | IDH_AV51-12_CLOSE |  |  | OMR_GW2.IDH.IR38.2 | IR38.2 | IR38.2
DO | IDH_AV51-12_OPEN |  |  | OMR_GW2.IDH.IR38.3 | IR38.3 | IR38.3
DO | IDH_AV51-13_CLOSE |  |  | OMR_GW2.IDH.IR38.4 | IR38.4 | IR38.4
DO | IDH_AV51-13_OPEN |  |  | OMR_GW2.IDH.IR38.5 | IR38.5 | IR38.5
DO | IDH_12EF2_ZC_DO |  | IDH Economizer Zone2 valve Output | OMR_GW2.IDH.IR39.02 | IR39.02 | IR39.02
DI | SWECO_VALVE_1 |  | N/C TO FINE GRINDER | OMR_GW2.IDH.IR39.08 | IR39.08 | IR39.08
DI | SWECO_VALVE_2 |  | N/O TO 7 MESH | OMR_GW2.IDH.IR39.09 | IR39.09 | IR39.09
DI | SWECO_VALVE_3 |  | N/O TO 7 MESH | OMR_GW2.IDH.IR39.10 | IR39.10 | IR39.10
DI | SWECO_VALVE_4 |  | N/C TO FINE GRINDER | OMR_GW2.IDH.IR39.11 | IR39.11 | IR39.11
DO | IDH_12EF2_ZH_DO |  | IDH Economizer Zone2 valve Opened | OMR_GW2.IDH.IR42.08 | IR42.08 | IR42.08
DA | CHILLER#1_COMP#1 |  | chiller #1 comp #1 | OMR_GW2.IDH.IR42.1 | IR42.1 | IR42.1
DA | CHILLER#1_COMP#2 |  | chiller #1 comp #2 | OMR_GW2.IDH.IR42.2 | IR42.2 | IR42.2
DA | CHILLER#1_COMP#3 |  | chiller #1 comp #3 | OMR_GW2.IDH.IR42.3 | IR42.3 | IR42.3
DA | CHILLER#1_COMP#4 |  | chiller #1 comp #4 | OMR_GW2.IDH.IR42.4 | IR42.4 | IR42.4
DA | CHILLER#1_COMP#5 |  | chiller #1 comp #5 | OMR_GW2.IDH.IR42.5 | IR42.5 | IR42.5
DA | CHILLER#1_COMP#6 |  | chiller #1 comp #6 | OMR_GW2.IDH.IR42.6 | IR42.6 | IR42.6
DA | PU-51-1A_PROVE |  | chiller #1 recirc pump A | OMR_GW2.IDH.IR43.0 | IR43.0 | IR43.0
DA | PU-51-2A_PROVE |  | chiller #2 recirc pump A | OMR_GW2.IDH.IR43.10 | IR43.10 | IR43.10
DA | PU51-2B_PROVE |  | chiller #2 recirc pump B | OMR_GW2.IDH.IR43.12 | IR43.12 | IR43.12
DA | PU52-2A_PROVE |  | small cooling tower recirc pump A | OMR_GW2.IDH.IR43.14 | IR43.14 | IR43.14
DA | PU-51-1B_PROVE |  | chiller #1 recirc pump B | OMR_GW2.IDH.IR43.2 | IR43.2 | IR43.2
DA | PU52-2B_PROVE |  | small cooling tower recirc pump B | OMR_GW2.IDH.IR44.0 | IR44.0 | IR44.0
DI | INTAKE_BOTTOM_CLOSED |  | Intake bottom valve closed feedback | OMR_GW2.IDH.IR44.08 | IR44.08 | IR44.08
DI | INTAKE_MIDDLE_CLOSED |  | Intake middle valve closed feedback | OMR_GW2.IDH.IR44.09 | IR44.09 | IR44.09
DI | ZONE2_EXHAUST_FEEDBACK |  | Zone2 valve exhaust feedback | OMR_GW2.IDH.IR44.10 | IR44.10 | IR44.10
DI | ZONE2_REC_FEEDBACK |  | Zone2 recirculation feedback | OMR_GW2.IDH.IR44.11 | IR44.11 | IR44.11
DI | ZONE4_EXHAUST_FEEDBACK |  | Zone4 exhaust feedback | OMR_GW2.IDH.IR44.12 | IR44.12 | IR44.12
DI | ZONE4_REC_FEEDBACK |  | Zone4 recirculation feedback | OMR_GW2.IDH.IR44.13 | IR44.13 | IR44.13
DO | CHEM_PARK_POS_DRIER |  | Chemetator Park Position to Drier | OMR_GW2.IDH.IR500.04 | IR500.04 | IR500.04
DI | DRIER_FLOW_PULSE_IN | DRIER_FLOW_PULSE_OUT | Pulse from Flowmeter to SCADA | OMR_GW2.IDH.IR500.05 | IR500.05 | IR500.05
DI | SWECO_7MESH_SELECTION |  |  | OMR_GW2.IDH.IR500.06 | IR500.06 | IR500.06
DI | SWECO_8MESH_SELECTION |  |  | OMR_GW2.IDH.IR500.07 | IR500.07 | IR500.07
DI | SWECO_20MESH_SELECTION |  |  | OMR_GW2.IDH.IR500.08 | IR500.08 | IR500.08
DI | SWECO_40MESH_SELECTION |  |  | OMR_GW2.IDH.IR500.09 | IR500.09 | IR500.09
DO | CHEM_OSCILLATING_DRIER |  | Chemetator Park Position to Drier | OMR_GW2.IDH.IR500.14 | IR500.14 | IR500.14
DI | SWECO_7MESH_INDICATION | SWECO_7MESH_SEL_TDS |  | OMR_GW2.IDH.IR501.00 | IR501.00 | IR501.00
DI | SWECO_8MESH_INDICATION | SWECO_8MESH_SEL_TDS |  | OMR_GW2.IDH.IR501.01 | IR501.01 | IR501.01
DI | SWECO_20MESH_INDICATION | SWECO_20MESH_SEL_TDS |  | OMR_GW2.IDH.IR501.02 | IR501.02 | IR501.02
DI | SWECO_40MESH_INDICATION | SWECO_40MESH_SEL_TDS | SWECO 40/20M Indication | OMR_GW2.IDH.IR501.03 | IR501.03 | IR501.03
DI | SWECO_40MESH_S_SELECTION |  |  | OMR_GW2.IDH.IR501.05 | IR501.05 | IR501.05
DI | SWECO_40MESH_S_INDICATION | SWECO_40MESH_S_SEL_TDS | SWECO 40/7M Indication | OMR_GW2.IDH.IR501.07 | IR501.07 | IR501.07
DI | SWECO_8MESH_S_SELECTION |  |  | OMR_GW2.IDH.IR501.08 | IR501.08 | IR501.08
DI | SWECO_8MESH_S_INDICATION | SWECO_8MESH_S_SEL_TDS |  | OMR_GW2.IDH.IR501.10 | IR501.10 | IR501.10
DI | STERILIZER_OZONE_ALM |  | Sterilizer Ozone Leak Alarm | OMR_GW2.IDH.IR501.11 | IR501.11 | IR501.11
DI | SWECO_WALTER_MESH_SELECTION |  |  | OMR_GW2.IDH.IR501.12 | IR501.12 | IR501.12
DI | SWECO_WALTER_MESH_INDICATION | SWECO_WALTER_SEL_TDS |  | OMR_GW2.IDH.IR501.14 | IR501.14 | IR501.14
DI | STERILIZER_OZONE_ALM2 |  | Sterilizer Ozone Trouble Alarm | OMR_GW2.IDH.IR501.15 | IR501.15 | IR501.15
DA | CHILLER_NOT_RUNNING |  | Carrier Chiller Not Running | OMR_GW2.IDH.IR502.0 | IR502.0 | IR502.0
DI | SWECO_REGRINDING_SELECTION |  |  | OMR_GW2.IDH.IR502.03 | IR502.03 | IR502.03
DI | SWECO_REGRINDING_INDICATION | SWECO_REGRIND_SEL_TDS |  | OMR_GW2.IDH.IR502.05 | IR502.05 | IR502.05
DA | IDH_SATAKE_LSHH1 |  | Satake Level Switch 1 High High | OMR_GW2.IDH.IR503.00 | IR503.00 | IR503.00
DA | IDH_SATAKE_LSH1 |  | Satake Level Switch 1 High | OMR_GW2.IDH.IR503.01 | IR503.01 | IR503.01
DA | IDH_SATAKE_LSH2 |  | Satake Level Switch 2 High | OMR_GW2.IDH.IR503.02 | IR503.02 | IR503.02
DA | IDH_SATAKE_FAULT |  | Satake Fault | OMR_GW2.IDH.IR503.03 | IR503.03 | IR503.03
DI | IDH_SATAKE_SILENCE_PB |  | SATAKE Alarm Silence P.B. | OMR_GW2.IDH.IR503.04 | IR503.04 | IR503.04
DI | IDH_SATAKE_CNTR_RESET_PB |  | SATAKE Counter Reset PB | OMR_GW2.IDH.IR503.06 | IR503.06 | IR503.06
DI | IDH_SATAKE_STOP_BELT | DRY_STOP_COMIL_FROM_SATAKE | SATAKE Command to Stop Comil | OMR_GW2.IDH.IR503.07 | IR503.07 | IR503.07
DI | IDH_SATAKE_CNTR_STOP_PB |  | SATAKE Counter Stop and Reset P.B. | OMR_GW2.IDH.IR503.08 | IR503.08 | IR503.08
DI | IDH_SATAKE_SILENCE |  | SATAKE Alarm Silence Status | OMR_GW2.IDH.IR503.10 | IR503.10 | IR503.10
DI | IDH_SATAKE_CNTR_STOP |  | SATAKE Counter Status | OMR_GW2.IDH.IR503.11 | IR503.11 | IR503.11
DI | IDH_SATAKE_BYPASS_MODE |  | SATAKE Bypass Mode - Prevent Comil Stopping on LSHH1 | OMR_GW2.IDH.IR503.12 | IR503.12 | IR503.12

## Trend List
Chart Group Name | Used on screen | Group Linked | Tags included | PLC Tags included
IDH Burner | IDH Mimic | Rect624 | DRY_DEWPOINT_AI DRY_DEWPOINT_SIGN IDH_BURNER_GAS RGN_BNR_01_AIR_TEMP IDH_BURNER_GAS_TOTALIZER T51-1 T51-5 DRY_D_12TT1_I
IDH Dewpoint | IDH Mimic | 149 | DRY_DEWPOINT_AI DRY_DEWPOINT_SIGN IDH_BURNER_GAS RGN_BNR_01_AIR_TEMP DRY_D_12TT1_I
IDH Small Cooling Tower | IDH Mimic | Polygon280, Polygon1 | T51-3 T51-3_STPT T51-3_OUT_PID_CA T52-48 T52-49 T52-50 PU-51-2A_PROVE CTL_FAN_SPEED CTS_FAN_SPEED
IDH T51-1 | IDH Mimic | 515, Rect1751, Rect1757, Rect1756, Rect1749 | RH51-1 T51-11 T51-10 T51-12 PU-51-1A_PROVE PU-51-1B_PROVE T51-4_T51-1_DELTA
IDH T51-12 | IDH Mimic | Rect1834 | T51-12 T51-12_STPT T51-12_OUT_PID_CA T51-3 T51-4
IDH T51-12 NEW | IDH Mimic | 555 | EVAP_IDH_TIC51_3_SP EVAP_IDH_TT51_3_PV EVAP_IDH_TIC51_3_CV EVAP_IDH_TIC51_3_MAN_CV EVAP_IDH_TT51_12_PV T51-4
IDH T51-2 | IDH Mimic | Rect1750 | T51-2 T51-2_STPT PU-51-2A_PROVE L52-51 T51-2_OUT_PID_CA
IDH T51-3 | IDH Mimic | Rect1755 | IDH_T51-3_PV_CA IDH_T51-3_OUTPUT IDH_T51-3_SETPOINT IDH_T51-3_PID_AUTO_MAN DRY_D_12TT1_I
IDH T51-3 NEW | IDH Mimic | Rect1929 | EVAP_IDH_TT51_3 EVAP_IDH_TIC51_3_SP EVAP_IDH_TIC51_3_CV EVAP_IDH_TIC51_8_SP EVAP_IDH_TIC51_8_CV DRY_D_12TT1_I
IDH T51-5 | IDH Mimic | Rect533 | T51-5 T51-5_STPT T51-5_OUT_PID_CA IDH_REGEN_FAN_AMPS IDH_MAIN_FAN_AMPS
IDH T51-8 NEW | IDH Mimic | 556 | EVAP_IDH_TT51_3 EVAP_IDH_TIC51_8_SP EVAP_IDH_TIC51_8_CV EVAP_IDH_TIC51_8_MAN_CV T51-4
IDH Temperatures | IDH Mimic | 245 | RH51-1 T51-4 T51-1 T51-2 T51-6 T51-3 DRY_D_12TT1_I T51-5
IDH Total | IDH Mimic | 514 | IDH_GAS_DAILY_TOT IDH_BURNER_GAS IDH_BURNER_GAS_TOTALIZER IDH_GAS_MONTHLY_TOT

## PLC_LOGIC
Total rungs | 227
Rung (Range) | Name/Comment | Usage/Description | Other Notes
| Control Steam | TIC51-3 / T51-3 / TCV51-3 | Heats in winter
| Control Cooling | TIC51-8 / T51-8 / TCV51-8 | Cools
| Control of P117 |  | Look into this - this pump is on sterilizer
| Control of P66 |  | Look into this - this pump is on sterilizer
12-14 | Flow rates for alarms
Delta calculation
| P117 Setpoint (DM3501) | P117 setpoint is set (MOV) and compared against | This would logically be moved to Sterilizer
| P66 Setpoint (DM3500) | P66 setpoint is set (MOV) and compared against | This would logically be moved to Sterilizer
0 |  | Adds/Compares with 3005, 3006, 3007